## Sheet1
Mxorder_No | Mx_Procedure | Classification | Create_Comments | Assigned_To | Activity | Account | Project | Crew_Type | Gen_Type | Generated_By | Schedule_Date | Completion_Date | Orig_Location | Composite | Related | Parent_Mxorder_No | Mx_Procedure_Type | Max_Equip_Health | Passport_W_o | Out_Of_Service_On | Back_In_Service_On | Due_Date | Days_Until_Due | Overdue_Date | Grace_Period_Days | Archive_Text
2009-1970001979 | 2Planned CM Diagnostic Tx GSU | Unclassified | 10-06-09 -- WWK -- Get cooler/fan info for material specialists from ALL coolers on #2 GSU @ Big Bend power plant -- relayed same to butera -- [MxOrder - 2009-1970001979 / 2Planned CM Diagnostic Tx GSU] |  | Diagnostic | Lite Truck | P3 | Lite Truck | Manual | KING, WILLIAM (BILLY) |  | 2009-10-06 11:09 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-2990013727 | 2Planned CM Diagnostic Tx GSU | Unclassified | NEED DGA FOR TECO LAB.GNM 2/15/00 3/16/00JIM COMPLETE {MxOrder - 2000-2990013727 / 2Planned CM Diagnostic Tx GSU} | URBANIK, JAMES | Diagnostic | Lite Truck |  | Lite Truck | Manual |  | 2000-02-16 | 2000-03-16 09:22 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
1999-2990008839 | COOLER WASHING PM - TxGSU | Unclassified | 03/03/99 ROCAMORA, STARTED TX COOLER WASHING--03/04/99 ROCAMORA, COMPLETED TX COOLER WASHING. WJF {MxOrder - 1999-2990008839 / COOLER WASHING PM} | ROCAMORA, ALBERT | Maintenance | Maintenance 2 Man Crew |  | Maintenance 2 Man Crew | Automatic |  |  | 1999-03-04 16:13 | BIG BEND | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
1999-2990008467 | 2Planned CM Minor Tx GSU | Unclassified | W.O. #19981395 - R. POTTER - 6/11/98 REPAIR OIL LEAK ON NEW DRAIN VALVE INSTALLED ON BANK # 5, FOR REMOVING OIL FROM COOLER.ALSO CHECK DRAIN VALVE BANK # 1 & 4. REPAIRED ALL VALVES EXCEPT 1 BOTTOM AND 2 TOP VALVES. WILL REQUIRE REMOVAL OF OIL FROM TX TO REPLACE REMAINDER OF VALVES. 2/12/99 - TLT CREATED NEW MX ORDER W/ NEW MX PROCEDURE, IML {MxOrder - 1999-2990008467 / 2Planned CM Minor Tx GSU} |  | Maintenance | Maintenance 4 Man Crew |  | Maintenance 4 Man Crew | Manual |  |  | 1999-03-29 06:45 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2007-2980001133 | 2Planned CM Minor Tx GSU | Unclassified | Changed out the nitrogen bottle and cleaned fittings and applied liquid teflon to prevent leakage. 12-20-07 DBCWB . [MxOrder - 2007-2980001133 / 2Planned CM Minor Tx GSU] | BLEDSOE, CHARLES (WAYNE) | Maintenance | Lite Truck | P3 | Lite Truck | Manual | BLEDSOE, CHARLES (WAYNE) |  | 2007-12-20 15:34 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2007-1990001837 | 2Planned CM Minor Tx GSU | Unclassified | Replaced the nitrogen bottle and ordered 6 spares for the plant. 3-30-07 DBCWB . [MxOrder - 2007-1990001837 / 2Planned CM Minor Tx GSU] | BLEDSOE, CHARLES (WAYNE) | Maintenance | Lite Truck | P3 | Lite Truck | Manual | BLEDSOE, CHARLES (WAYNE) |  | 2007-03-30 08:55 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2007-1990001953 | 2Planned CM Minor Tx GSU | Unclassified | Changed out the nitrogen bottle and pumped up the tires on the bottle cart. 10-19-07 DBCWB . [MxOrder - 2007-1990001953 / 2Planned CM Minor Tx GSU] | BLEDSOE, CHARLES (WAYNE) | Maintenance | Lite Truck | P2 | Lite Truck | Manual | BLEDSOE, CHARLES (WAYNE) |  | 2007-10-19 10:16 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2002-2890000632 | 2Planned CM Minor Tx GSU | Unclassified | CHANGED NITROGEN BOTTLE.2/7/02,GEF [MxOrder - 2002-2890000632 / 2Planned CM Minor Tx GSU] | FERNANDEZ, GUSTAVO | Maintenance | Lite Truck |  | Lite Truck | Manual | FERNANDEZ, GUSTAVO |  | 2002-02-07 09:50 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2006-1980001459 | 2Planned CM Minor Tx GSU | Unclassified | 3/19/06 thermal OL for coolers 2,4,6, triped. they also triped last night. the controll Cab. was verry hot. pull the two 480v. fuses that feed directly to two large heaters in bottom of the Cab. it looks like these heaters were added on. reset OL relays. for winter time need to either install a thermoste to controll temperture. are put in smaller heater. dbfgk [MxOrder - 2006-1980001459 / 2Planned CM Minor Tx GSU] | HARRELL, KENNETH | Maintenance | Maintenance 3 Man Crew | P2 | Lite Truck | Manual | KINSMAN, FORREST (WOODY) |  | 2006-03-22 14:07 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2003-1990001083 | 2Planned CM Minor Tx GSU | Unclassified |  | BLEDSOE, CHARLES (WAYNE) | Maintenance | Lite Truck |  | Lite Truck | Manual | BLEDSOE, CHARLES (WAYNE) |  | 2003-11-15 11:42 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2006-1990001647 | 2Planned CM Minor Tx GSU | Unclassified | Changed out the nitrogen bottle. 6-10-06 DBCWB . [MxOrder - 2006-1990001647 / 2Planned CM Minor Tx GSU] | BLEDSOE, CHARLES (WAYNE) | Maintenance | Lite Truck | P3 | Lite Truck | Manual | BLEDSOE, CHARLES (WAYNE) |  | 2006-06-10 09:41 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2007-1990001800 | 2Planned CM Minor Tx GSU | Unclassified | Changed out the nitrogen bottle and leak checked same. 1-11-07 DBCWB . [MxOrder - 2007-1990001800 / 2Planned CM Minor Tx GSU] | BLEDSOE, CHARLES (WAYNE) | Maintenance | Lite Truck | P3 | Lite Truck | Manual | BLEDSOE, CHARLES (WAYNE) |  | 2007-01-11 11:33 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2002-1960000840 | 2Planned CM Minor Tx GSU | Unclassified | 12-18-002 TX. down for an outage and using nitrogen. We have replaced the nitrogen bottle three times in the last month. When the unit was up it did not use nitrogen. Need to arrange to have grounds installed and someone to take clearance on the #2 GSU to check the top for nitrogen leaks. Replaced the bottle today and hung an aluminum tag for future nitrogen leak work. McMinn. 12-21-002 Found the pressure relief (center) leaking at a good rate. As per Chip Hall we installed new gaskets on all three of the pressure reliefs. We used Buna-N "O" ring to re-gasket. Job completed. McMinn. [MxOrder - 2002-1960000840 / 2Planned CM Minor Tx GSU] | MCMINN, STEPHEN | Maintenance | Maintenance 3 Man Crew |  | Maintenance 3 Man Crew | Manual | MCMINN, STEPHEN |  | 2002-12-21 16:17 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2005-1960001107 | 2Planned CM Minor Tx GSU | Unclassified |  | HALL, EMMETT (CHIP) | Maintenance | Maintenance 2 Man Crew | P2 | Maintenance 2 Man Crew | Manual | BELL, HOWARD |  | 2005-03-08 14:17 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2020-3000161361 | 2Planned CM Minor Tx GSU | Unclassified | 10/26/20---LP gas alarm on Unit #2 GSU. The Dur cyl is empty and I hooked the regulator up to the (left hand) stand by Dura Cyl. it had been hooked up to a 3000 psi nitrogrn cyl. and I was told b Larry that they had lowered to pressure setting on the regulators being hooked up to high pressure cylinders. I left itas it was but being hooked up to a liquid filled Dura Cyl. it only produced around 20 psi not the 50 psi that is normal. That is enough to allow me to clear the alarm on the GSU. There is a spare Dura Cyl beside the Cardox tank but it will have to be moved into positio n for the regulator hose to reach and right now it is raining very hard. As is thee is the new full Dura Cyl. I hooked up and a full spare Dura Cyl. and 1 empty at this staton.---ecdkb [MxOrder - 2020-3000161361 / 2Planned CM Minor Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P2 | Lite Truck | Manual | BRYAN, DAVID |  | 2020-11-20 06:01 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 185 | [7 empty] | No Archive
2021-3000082398 | 2Planned CM Minor Tx GSU | Unclassified | 11/16/2021 Low pressure alarm. Swapped bottles and cleared alarm in control cabinet with toggle switch. Bissell [MxOrder - 2021-3000082398 / 2Planned CM Minor Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P1 | Lite Truck | Manual | BRANDON, BISSELL | 2021-11-16 07:51 | 2021-11-16 07:53 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 451 | [7 empty] | No Archive
2006-1890000245 | 2Planned CM Minor Tx GSU | Unclassified | 9-18-06 dbrsc top rad value not working . needs to be replaced, north bank, west cooler 10-18-06 CONDUIT ON THE NORTHSIDE OF THE TX. HAS OIL IN IT.(CONDUIT FOR FANS ANAD PUMP)CLEANED AND PUT OIL SOAK PADS UNDER IT.THE EAST RAD. PUMP IS LEAKING TIGHTENED ALL BOLTS AND ALLEN BOLTS ,NOTHING WAS LOOSE,.BELIEVE THE LEAK IS COMING FROM THE PUMP HOUSING SEAL.(WHERE THE PUMP MOTOR AND IMPELLAR BOLT TO THE HOUSING) CLEANED AND PUT OIL SOAK PADS AND A BUCKET UNDER IT. 10/19/06 berry replace pump plug and pump cord, middle cooler north side. parts ordered Gus, if you could, check in a couple of days and let me know exactly where the east pump is leaking so that we can order parts if needed. berry 10/19/06 After completion have building services clean up all oily residue. berry 10/19/06 Keeping the diaphers fresh. I've been changing them about every two weeks all year. 7-14-07 DBCWB . STEVE THE LEAK IS WHERE THE MOTOR BOLTS TO THE HOUSING. [MxOrder - 2006-1890000245 / 2Planned CM Minor Tx GSU]Q changed out oil pads.11-2,11-10 Changed out diaphers. 2-21-07 DBCWB . Replaced all diaphers and picked up trash around tx.. 4-8-07 DBCWB . Replaced diaphers again and wiped down pump. 4-21-07 DBCWB Changed out all diaphers. 5-18-07 DB WB ..Replaced diaphers , and drained water from the bucket under leaking oil pump. 6-6-07 DBCWB . Replaced the diaphers again. 8-10-07 DBCWB . Replaced diaphers under leaking conduit. 8-23-07 DBCWB . Replaced all diaphers under leaking pump and conduit. 9-15-07 DBCWB . Replaced diaphers. 10-4-07 DBCWB . Changed ouit all diaphers. 12-3-07 DBCWB . | MCCATTY, DONALD | Maintenance | Maintenance 3 Man Crew | P3 | Maintenance 3 Man Crew | Manual | COLEMAN, STEVE |  | 2009-04-21 18:04 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | 752778 | [6 empty] | No Archive
2002-1900000167 | 2Planned CM Minor Tx GSU | Unclassified |  | SMITH, GREGORY | Station | Lite Truck |  | Lite Truck | Manual | SMITH, GREGORY |  | 2002-10-25 18:09 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2002-1910000347 | 2Planned CM Minor Tx GSU | Unclassified |  | BERRY, STEVE | Maintenance | Maintenance 2 Man Crew |  | Maintenance 2 Man Crew | Manual | HENRY, ROSCO |  | 2002-10-24 11:31 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2010-1910000694 | 2Planned CM Minor Tx GSU | Unclassified | 02/08/10 removed grounds from #2 GSU [MxOrder - 2010-1910000694 / 2Planned CM Minor Tx GSU] |  | Maintenance | Maintenance 3 Man Crew | P3 | Lite Truck | Manual | HENRY, ROSCO |  | 2010-02-08 12:23 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2004-1930001412 | 2Planned CM Minor Tx GSU | Unclassified | 10/22/04--We have 5 empty nitrogen cylinders and no full spares. Please have 5 full bottles delivered Monday morning.--dbdkb 10/25/04--I met Mike at the station and we changed out two bottles on the tx's at the back of the plant and he delivered the five other full bottles and picked up the other 5 empty bottles.----dbdkb [MxOrder - 2004-1930001412 / 2Planned CM Minor Tx GSU] | MCLEOD, RALPH | Maintenance | Maintenance 3 Man Crew | P2 | Maintenance 3 Man Crew | Manual | BRYAN, DAVID |  | 2004-11-08 10:20 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2010-1940002766 | 2Planned CM Minor Tx GSU | Unclassified | 7/28/10----The winding and oil temperature gauges are mounted above the control cabinet which itself is mounted above a platform. In order to reach these gauges we have to stand on the hand rails. Please have the gauges relocated to a safe to reach position. SAFETY.----dbdkb [MxOrder - 2010-1940002766 / 2Planned CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Maintenance 3 Man Crew | Manual | BRYAN, DAVID |  | 2012-05-02 17:11 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
1999-1960000266 | 2Planned CM Minor Tx GSU | Unclassified | 11/10/99 CHANGE OUT NITROGEN BOTTLE DBMGL. {MxOrder - 1999-1960000266 / 2Planned CM Minor Tx GSU} | LUPER, MICHAEL | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 1999-11-10 15:37 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1960000443 | 2Planned CM Minor Tx GSU | Unclassified | 08/18/00 FAN NOT RUNNING #2 GSU INSTALL NEW FAN MOTOR RAN FOR A FEW MINS.I CALL FOR A NEW MOTOR AND INSTALLED RUNS FINE.DBMGL/DBJU FANS IN SHOP FOR REPAIR. GOULD CENTURY/ TYPE SC, CODE 1, RPM 870, HP 1, 230/480 VOLTS,. 3 PHASE, PART 6-338154-40, FR 184T. RELIANCE/ TYPE P, 3 PHASE, ID#P18G6570C, HP 1, RPM 870, 240/480 VOLTS. job completed. tmrgk. 08/22/2000 {MxOrder - 2000-1960000443 / 2Planned CM Minor Tx GSU} | KELLY, GLENN | Maintenance | Shows - Preview |  | Lite Truck | Manual |  |  | 2000-08-22 09:25 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2011-3000180583 | 2Planned CM Minor Tx GSU | Unclassified | 7/15/11. BIG BEND CALLED AND REQUESTED GROUNDS ON # 2 GSU. FOR WORK TO START ON UNIT AT 0700HRS.SAT.7/16/11. UNIT WAS NOT SWITCHED AND TAGGED. CREW HAD TO SWITCH UNIT OUT THEN GROUND.7/18/11. CREW CALLED OUT AND REMOVED GROUNDS . HARRELL ON CALL. [MxOrder - 2011-3000180583 / 2Planned CM Minor Tx GSU] | HARRELL, KENNETH | Gen Interconnect Facility | Generation Interconnect Facilities | P2 | Maintenance 2 Man Crew | Manual | MCCATTY, DONALD | 2011-07-16 07:44 | 2011-07-19 07:58 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2010-1940002847 | 2Planned CM Minor Tx GSU | Unclassified | 11/18/10---SAFETY----The existing platform is to small to allow a person to get away from the equipment inside the control cabinet if there was a fire. The doors when opened contribute to the problem and the plant has installed a spring loaded door on the platform which contributes to the problem. Please have the platform enlarged.-----dbdkb [MxOrder - 2010-1940002847 / 2Planned CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Maintenance 3 Man Crew | Manual | BRYAN, DAVID |  | 2016-04-15 09:09 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 7149 | [7 empty] | No Archive
2013-3000020490 | 2Planned CM Minor Tx GSU | Unclassified | 2/19/13 etm alarm fail,etm wont show temp for winding or top oil, called shawn, Shawn looked at etmcleared alarm but temp is still off , need to monitor, let Urbanik know.. Coleman/Wiggins [MxOrder - 2013-3000020490 / 2Planned CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Lite Truck | Manual | COLEMAN, STEVE |  | 2016-07-06 11:36 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 8364 | [7 empty] | No Archive
2017-3000022838 | 2Planned CM Minor Tx GSU | Unclassified | 8-16-17-- Ran pumps and fans for Post Outage inspection. C/O oil pads inside control cabinet, and worked on Oil Pump gauges. Found 1 cracked gauge and 1 not functioning properly. Will return on 8-17-17 to finish C/O. RSC/JBG [MxOrder - 2017-3000022838 / 2Planned CM Minor Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P3 | Lite Truck | Manual | COLEMAN, STEVE |  | 2018-02-13 09:46 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 22715 | [7 empty] | No Archive
2020-3000012136 | 2Planned CM Minor Tx GSU | Unclassified | 1-13-20 2 GSU fan on top bank 1 not working Absher / Newsome [MxOrder - 2020-3000012136 / 2Planned CM Minor Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P3 | Lite Truck | Manual | ABSHER, LARRY |  | 2021-10-14 09:58 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 67691 | [7 empty] | No Archive
1999-1880000017 | MINOR PM - TxGSU | Unclassified | 10-27-99 cleaned and siliconed all bushings, insulators, and arrestors to#2 gsu....larry smith {MxOrder - 1999-1880000017 / MINOR PM} | SMITH, LARRY | Maintenance | Doble 4 Man Crew |  | Maintenance 4 Man Crew | Manual |  |  | 1999-10-27 17:01 | BIG BEND | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
1999-2990008840 | TxGSU – Transformer Yearly Oil Test (DGA and Fluid Quality) | Unclassified | HARTFORD OIL SAMPLE TAKEN. KDH 4/14/99 {MxOrder - 1999-2990008840 / DGA PM Tx - Hartford Lab} | HARRELL, KENNETH | Diagnostic | Lite Truck |  | Lite Truck | Automatic |  |  | 1999-04-14 13:44 | BIG BEND | N | 0 |  | Preventive Maintenance | 3862 |  | 1999-04-14 13:42 | 1999-03-29 12:43 |  |  |  |  | No Archive
2000-2990014171 | TxGSU – Transformer Yearly Oil Test (DGA and Fluid Quality) | Unclassified | 3/24/00JIM COMPLETE {MxOrder - 2000-2990014171 / DGA PM Tx - Hartford Lab} | URBANIK, JAMES | Diagnostic | Lite Truck |  | Lite Truck | Automatic |  |  | 2000-03-24 12:59 | BIG BEND | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
1999-2990011596 | TxGSU – Transformer Yearly Oil Test (DGA and Fluid Quality) | Unclassified | 10/26/99 HARTFORD OIL SAMPLE TAKEN DBMGL. {MxOrder - 1999-2990011596 / DGA PM Tx - Hartford Lab} | LUPER, MICHAEL | Diagnostic | Lite Truck |  | Lite Truck | Automatic |  |  | 1999-10-26 14:43 | BIG BEND | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2006-2990049025 | 2Planned CM Cooler Washing Tx GSU | Unclassified | 4/28/06. TX. HAS OIL TEMP. ALARM. MEMO FOR OPERATIONS TO KEEP OIL TEMP BELOW 95 DEGREES CENTIGRADE. ARRIVED TO WASH COOLERS AND FOUND HOT SPOT ALARM. OIL TEMP WAS 105 DEGREES AND WINDING TEMP WAS 122. PLANT TOOK SOME LOAD OFF TO LOWER TEMP. JEREMY CALKINS PRESSURED WASHED THE LOWER THIRD OF THE COOLERS. WILL NEED OUTAGE TO WASH THE COOLERS. DGA SAMPLED TX. D. MCCATTY. [MxOrder - 2006-2990049025 / 2Planned CM Cooler Washing Tx GSU] 5/25/06 HI TEMP ALM IN . ESO CALLED ME TO CHECK ON IT . WHEN I ARRIVED ALL PUMPS AND FANS RUNNING PLANT PERSONEL INFORMED ME THAT THEY NEVER STOPPED. OPERATIONS HAD SHED SOME LOAD SO TEMP HAD DROPPED SOME OIL 85 ACT, 105 DRAG HAND . WINDING 100 ACT DRAG HAND 120 . I RESET THEM AND CONTINUED TO MONITOR TEMP. UNTIL ALM CLEARED. DBMHC 6/1/06 COOLER WASHING COMPLETE. DBGHP | MEDICH, GEORGE | Maintenance | Maintenance 2 Man Crew | P3 | Maintenance 2 Man Crew | Manual | MCCATTY, DONALD |  | 2006-06-15 17:28 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000040233 | 1Emergency CM Diagnostic Tx GSU | Unclassified | 2\17\12 COOLER BANK #3 NOT RUNNING EVEN WITH COOLERS IN MANUAL. 2\17\12 INSTALLED NEW COIL IN FAN CONTACTOR#3 ITS A GOOD CONTACTOR SWITCH.ABZWR [MxOrder - 2012-3000040233 / 1Emergency CM Diagnostic Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | RAY, ZACHARY |  | 2012-02-17 11:37 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2013-3000040650 | 1Emergency CM Diagnostic Tx GSU | Unclassified | 6\1\13 high oil temp alarm.oil temp is only 84 deg c.the set point for this alarm is 95 deg c.talked with maccatty and kiepke about this.kiepke is concerned about the var level.this will cause the tx to get very hot very.the tx did send an alarm to control room and has not dropped all the way back down to reset value on the etm according to kiepke.alarm will clear as it cools down.abzwr [MxOrder - 2013-3000040650 / 1Emergency CM Diagnostic Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | RAY, ZACHARY |  | 2013-06-02 15:27 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2014-3000060883 | 1Emergency CM Diagnostic Tx GSU | Unclassified | 12-1-12 Plant had a Loss of Oil flow on GSU Unit 2. Found #2 bank in alarm. Reset the right thermal on the #4 relay then reset the alarm. All of the fans and pumps were now running. Tested #4 relay feeds A phase was 13.74 amps, B was 13.76, and C was 13.71 which is around what all the other relays are reading . MTM had reset the same thermal earlier today. The right thermal on the #4 relay needs to be replaced. BTB 12-2-14... c/o thermal on #4 contactor. N31. spare thermals in bottom of cab. mtm/rock [MxOrder - 2014-3000060883 / 1Emergency CM Diagnostic Tx GSU] 12-12-14 plant had alarm come in on loss of power had bad volt on 1 leg on emergy source sidecomeing from [plant plant pulled on cb that feeds tx 480 and found buss bar and fingers were burnt up plant will fix there part left fans on man |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P3 | Lite Truck | Manual | BALFOUR, BRIAN |  | 2015-06-02 09:17 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2013-3000000158 | 1Emergency CM Diagnostic Tx GSU | Unclassified | 3/7/2013- D OO19150 -Loss of AC alarm and Loss of Oil Flow Bank 1 Alarm. The problem is believed to be associated with the coil in the top 2 left contactors. They are both rated for 575-600 volts and we are putting 480 to them. The normal source coil appears to be burnt up because when the normal source breaker in the plant is open all alarms clear. Tom Blair will find the correct coil and Harrell or Urbanik will get it installed. 3-12-12 dbrsc put new coilsl in cab for contactor 480 volt to replace 570/600- [MxOrder - 2013-3000000158 / 1Emergency CM Diagnostic Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | GARLAND, TIMOTHY |  | 2014-09-18 13:37 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2014-3000000304 | 1Emergency CM Minor Tx GSU | Unclassified | 5/18/14---Low Nitrogen cylinder alarm.The pressure on the system is 49 psi and the alarm is supposed to come in at 28 psi. I took the pressure gauge off and exercised the contact switch and the alarm cleared. The pressure on the gauge is not matching the other gauges. The pressure is 54 psi on the gauge...Garland [MxOrder - 2014-3000000304 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P1 | Lite Truck | Manual | GARLAND, TIMOTHY |  | 2014-09-18 13:40 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000010128 | 1Emergency CM Minor Tx GSU | Unclassified | 4/29/12 REMOVED GROUNDS #2 GSU @ BIG BEND. G.RAULERSON G.PAUL M.CHICO. G.PAUL 8/3/12 REMOVED GROUNDS #2 GSU @ BIG BEND...ABSHER / GARLAND [MxOrder - 2012-3000010128 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | PAUL, GILBERT |  | 2012-08-03 15:19 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000000077 | 1Emergency CM Minor Tx GSU | Unclassified | 6/15/12--ETM FAILURE ALARM was in. There were no fans running, the ETM was reading 78C on both temps. I put the fans in maual and all the fans came on. I left the fans in manual. The alarms cleared. The Unit tripped around 2200 but was still at 78 C at 0100 and no fans running. 6/15/12----There was not an alarm light on in the ETM and the control room also did not show an ETM related alarm. The unit tripped last nigh about 9 PM so when Tim arrived the unit was off line so the fans and pumps would not have been running. As per Jim Urbanik I am closing this mx order.----ecdkb [MxOrder - 2012-3000000077 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | GARLAND, TIMOTHY |  | 2012-06-15 09:34 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000020197 | 1Emergency CM Minor Tx GSU | Unclassified | 05/04/12 RSC/JBH -- ETM alarm// rebooted ETM cleared alarm//fans pumps ran okay// [MxOrder - 2012-3000020197 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | COLEMAN, STEVE |  | 2012-05-04 10:53 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000020223 | 1Emergency CM Minor Tx GSU | Unclassified | 6/13/12 C/O bottom fan motor on bank #1 TMK/RSC [MxOrder - 2012-3000020223 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | COLEMAN, STEVE |  | 2012-06-13 17:21 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2013-3000020596 | 1Emergency CM Minor Tx GSU | Unclassified | 5-1-8-13 DBRSC HAD OIL FLOW ALARM ON BANK 1 @ 5 BB # 2GSU RESET CB AND CONTACTORS IN CAB AND A/C SWAP OVER CHADDER FOR 2 OR 3 MIN THEN IT WAS OK [MxOrder - 2013-3000020596 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | COLEMAN, STEVE |  | 2014-09-18 13:39 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2013-3000020608 | 1Emergency CM Minor Tx GSU | Unclassified | 5-15-13 dbrsc mw doo19150 plant loss pri a/c source and trip off cb to fans had hi temp alarm turned on cb let tx cool down 5-15-13--- checked oil temp, was down to 79* celcius,all fans and pumps running, alarm was in then cleared shortly after i arrived, reset alarm light in cabinet---hutch [MxOrder - 2013-3000020608 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | COLEMAN, STEVE | 2013-05-15 15:41 | 2014-09-18 13:39 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2014-3000020985 | 1Emergency CM Minor Tx GSU | Unclassified | 4-24-14 dbrsc nit alarm on # 2 main and 2 a ss stx had to clear alarms by reset the alarms in cabs had crumpton delever new nit bottles and i think he must have bleed all nit off header for got to turn off valve [MxOrder - 2014-3000020985 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P3 | Lite Truck | Manual | COLEMAN, STEVE |  | 2014-09-18 13:38 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000070272 | 1Emergency CM Minor Tx GSU | Unclassified | 10-2-12---called out per palm river and plant, had a loss of power alarm on #2 main tx---reset toggle switch-----hutch [MxOrder - 2012-3000070272 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | HUTCHINSON, JOSEPH |  | 2012-12-19 09:41 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2011-3000080056 | 1Emergency CM Minor Tx GSU | Unclassified | 9-7-11 PLANT REPORTED A FAN GOING OUT. I REMOVED WIRES FROM TOP FAN ON #3 & ODERED FAN MOTOR. ROCK 9/12/11 found another bad fan motor bank #1 miller [MxOrder - 2011-3000080056 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P2 | Lite Truck | Manual | ROCAMORA, ALBERT |  | 2011-09-13 15:16 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000080161 | 1Emergency CM Minor Tx GSU | Unclassified | 03/28/12 CALLED OUT FOR HIGH TEMP ALARM UPON ARRIVAL FOUND ALL FANS AND PUMPS RUNNING. THE PLANT HAD PLACED ALL THE FANS ON MANUAL. THEY FOUND BANK NUMBER 3 OFF LINE.UPON CHECK OF BANKS FOUND THAT 3 BANKS WHERE OFF AT A TIME NOT ONE. LEFT FANS ON MANUAL WAITED FOR TEMP TO DROP. ALARM CLEARED RESET ALARM. NEEDS TO BE CHECKED WITH PRINTS TO DETERMINE WHY ALL FANS WONT COME ON, ON AUTO WILL CONTACT JIM URBANIK ROCK/JR found winding temp gauge bad will replace winding temp gauge during april outages ETM INSTALLED BY WIRE SHOP [MxOrder - 2012-3000080161 / 1Emergency CM Minor Tx GSU] | URBANIK, JAMES | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | ROCAMORA, ALBERT | 2012-03-29 00:31 | 2012-04-26 07:06 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000080169 | 1Emergency CM Minor Tx GSU | Unclassified | 4-11-12 #2 gsu low nit. alarm, found contact in press. gauge closed. plant cleared alarm and set toggle sw. in the middle. Need to replace gauge and put toggle sw. in normal position so plant will get alarm. mtm/ rock [MxOrder - 2012-3000080169 / 1Emergency CM Minor Tx GSU] | URBANIK, JAMES | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | ROCAMORA, ALBERT | 2012-04-11 21:21 | 2012-04-12 12:27 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000080183 | 1Emergency CM Minor Tx GSU | Unclassified | 5-2-12 high oil temp. al. #2gsu oil was 89c --oil al. in @ 85c & winding @ 115c -- winding was 116c. all fans & pumps were running. had plant back down on vars. rock [MxOrder - 2012-3000080183 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | ROCAMORA, ALBERT | 2012-05-02 17:12 | 2012-06-14 11:05 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000080305 | 1Emergency CM Minor Tx GSU | Unclassified | 11-1-12 ETM FAIL AL. RESET ETM & RESET AL. ROCK [MxOrder - 2012-3000080305 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | ROCAMORA, ALBERT | 2012-11-02 00:28 | 2012-12-19 09:38 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2011-3000110026 | 1Emergency CM Minor Tx GSU | Unclassified | 11/28/11 CALLED OUT TO REMOVE GROUNDS FROM #2 GSU.....ABSHER & Z.RAY [MxOrder - 2011-3000110026 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | ABSHER, LARRY |  | 2011-11-30 05:42 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000060181 | 1Emergency CM Minor Tx GSU | Unclassified | 01/03/12---Low Nitrogen Alarm. C/O M/T Cylinder. Ordered 6 full nitrogen cylinders to be delivered and the 4 M/T cylinders to be picked up.---ecdkb [MxOrder - 2012-3000060181 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | BRYAN, DAVID |  | 2012-01-03 04:59 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2014-3000110423 | 1Emergency CM Minor Tx GSU | Unclassified | 12/1/14 LOW OIL FLOW bank #2. thermal tripped on #4 contactor. reset breaker and contactor, all fans and pumps are running. reset alarm, cleared...mtm/rock [MxOrder - 2014-3000110423 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P1 | Lite Truck | Manual | MEIGHEN, MICHAEL |  | 2014-12-01 16:33 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2010-2990067222 | 1Emergency CM Minor Tx GSU | Unclassified | 1/3/10---PLANT REPORTED BANKS 1,3,5 WOULD NOT COME ON. THEY HAD OPERATED THE ACB 480 FOR THE FEED TO THOSE BANKS SERVERAL TIMES. 480 FEED TO TX. CABINET WAS GOOD. FOUND VOLTAGE MONITOR FOR THAT FEED WAS STUCK. OPERATED MONITOR SEVERAL TIMES TO FREE IT UP. ALL BANKS NOW OPERATING PROPERLY IN AUTOMATIC. OIL TEMP/66 c , WINDING TEMP 88 c. DKM/CKL. THIS MONITOR IS LOCATED IN THE SWAPOVER IN THE UPPER RIGHT HAND OF THE CABINET. DOES NOT HAVE A MONITOR LIGHT.--- DKM/CKL. 2/8/10---The coolers # 1,3 and 5 will not run. We checked the voltage from the supply contactor for all three coolers ( left side door, right side contactor ) and the contactor will not pick up. We checked the coil and it was ok. The contractors who installed the new coolers have done some re-wiring and it no longer matches the prints. Donnie suggested that we look at the voltage sensing relay behind the right side door and exersize it as he did before. We did and it did not appear to help. Jim thinks that the other banks of fans may still be picked up only after the field breaker on the exciter is closed. The unit is scheduled to come on line tomorrow and Jim said we will address it then.-----dbdkib 2/10/10----The unit came on line and the coolers still would not work. The indivisual cooler contactors are closing and opening with the manual and cooler selector switches but the supply contactor for coolers 1, 3 and 5 will not pick up. The voltage monitor for that contactor monitors the voltage for coolers 2, 4 and 6 and the way it is wired the contact 3-4 will not close unless you loose power to those coolers first. We lifted A phase wire to the monitor and taped it and when we did the green light on the monitor went off and it closed the contact 3-4 which picked up the coil in the voltage supply contactor for coolers #1,3,and 5. All fans and pumps will run in manual and in auto both banks of fans will run when selected. There are no alarms in on the GSU. Jim is going to check with engineering tomorrow. The prints are not accurate for the control cabinet and the control circuits for the coolers have been modified. -----dbdkb 2/19/10JIM, ORDERED NEW SET OF SWAP OVER CONTACTORS . TO BE INSTALLED NEXT OUTAGE 2/26/10---The unit is down now for a schedulede outage.---dbdkb 4/5/10 P.R. WANTED ME TO CHECKED OIL TEMP. @ 70 DEG. C. DBGP DBBDR 4/11/10 DID SAME OIL TEMP. @ 70 DEG. C. ALL FANS & PUMPS RUNNING. CHECKED ALARM IN TX. CONT. CAB. NO ALARM IN ALSO CHECKED ALARM LIGHT. CHECKED WITH CONT. ROOM THEY HAD NO ALARM ONLY IN @ P.R. REPORTED TO P.R. & G. RAULERSON. DBGHP 4/21/10----We started to install a new AB contactor but the replacement unit was not correct. Jim is ordering the correct contactor. The contactor that they recieved may work if we wire it as the print shows and can find lugs that will work.-----dbdkb 11/12/12---Thye tx was getting hot and the plant reported that three coolers were not running. We found coolers 1,3 and 5 not running. We lifted the A phase wire from the monito on the left set of swap-over contactors same as before to allow the emergency source to pick up. The way the fans are wired is coolers 2,4, and 6 are on one feed from the plant and 1,3 and 5 are on the other. We did not loose a source (feed) but the coil on the normal source of the left contactors is open so the swap-over did not have a reason to swap until we fooled it by lifting the A phase monitor wire. We tagged the wire and are ordering a replacement coil for the contactor. Jim Urbanik want's to change this at the next outage if not necessary to do while the unit is on line. Please land the A phase wire back on the voltage monitor after changing the coil.----ecdkb [MxOrder - 2010-2990067222 / 1Emergency CM Minor Tx GSU] 12/20/12 REMOVED A/C SWAPOVER CONTACT COIL,TRIED TO PUT NEW ONE IN, BUT WAS SENT WRONG ONE, REINSTALLED OLD ONE, A.STAFFORD HAS NEW COIL ON ORDER. RSC/JLC | URBANIK, JAMES | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | MCCATTY, DONALD |  | 2014-09-18 13:40 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2016-3000050617 | 1Emergency CM Minor Tx GSU | Unclassified | 12/22/16 Called to Big Bend for loss of oil flow on Unit 2. Found contact on fan and pump set 2 burned up. Someone from the plant turned the CB off for set 2. Called Glenn and it will be changed out in the morning. 3 out of the 6 sets of pumps and fans are running. Liquid temp is 75 and winding temp is 85. Predmore [MxOrder - 2016-3000050617 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P1 | Lite Truck | Manual | PREDMORE, BRYCE | 2016-12-22 19:58 | 2018-02-13 09:41 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 22715 | [7 empty] | No Archive
2018-3000011781 | 1Emergency CM Minor Tx GSU | Unclassified | 7-10-18 Nitrogen dewer bottle safety leak by, tapped on relief valve and cleard out trash. Absher/ Layton [MxOrder - 2018-3000011781 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective |  | Lite Truck | Manual | ABSHER, LARRY |  | 2018-07-10 10:09 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 28356 | [7 empty] | No Archive
2019-3000011910 | 1Emergency CM Minor Tx GSU | Unclassified | 1-10-19 Big Bend inert gas alarm, c/o dewer bottle & ordered a new bottle...Absher / Keys [MxOrder - 2019-3000011910 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective |  | Lite Truck | Manual | ABSHER, LARRY |  | 2019-01-10 08:19 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 36939 | [7 empty] | No Archive
2015-3000070823 | 1Emergency CM Minor Tx GSU | Unclassified | 8/29/15 Notified that the fans were off & there was smoke coming out of control cabinet on gsu #2 . Contactor coil for bank #5 is bad . Lifted a wire on the contactor coil for bank #5 and was able to run fans , left fans in manual also unplugged oil flow gauge for bank#5 so an alarm doesnt come in.Need to c/o contactor coil. ECTMK 8/29/15 C/O contactor coil on bank #5 , everything back normal [MxOrder - 2015-3000070823 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P1 | Lite Truck | Manual | KIDD, TONY | 2015-08-30 02:27 | 2015-09-01 11:31 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 4504 | [7 empty] | No Archive
2006-2980000984 | 1Emergency CM Minor Tx GSU | Unclassified |  | SMITH, GREGORY | Maintenance | Lite Truck | P1 | Lite Truck | Manual | SMITH, GREGORY |  | 2006-04-09 22:59 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | 704362 | [6 empty] | No Archive
2005-2980000757 | 1Emergency CM Minor Tx GSU | Unclassified |  | KINSMAN, FORREST (WOODY) | Maintenance | Lite Truck | P2 | Lite Truck | Manual | SMITH, GREGORY |  | 2005-02-14 10:48 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2005-2980000919 | 1Emergency CM Minor Tx GSU | Unclassified | 11/26/05 #2 Bank of fans has one set on south east corner not running,unit is coming down. needs to be addressed monday morning. DBDMH. -- THERMAL FOUND TRIPPED ON CONTACTOR, RESET BY D.HOWARD. 11/28/0 DBKDH [MxOrder - 2005-2980000919 / 1Emergency CM Minor Tx GSU] | HARRELL, KENNETH | Maintenance | Lite Truck | P2 | Lite Truck | Manual | HOWARD, DAVID |  | 2005-11-28 09:41 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2002-2890000639 | 1Emergency CM Minor Tx GSU | Unclassified | changed nitrogen bottle.4-4-02 [MxOrder - 2002-2890000639 / 1Emergency CM Minor Tx GSU] |  | Maintenance | Lite Truck |  | Lite Truck | Manual | FERNANDEZ, GUSTAVO |  | 2002-04-04 14:51 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2002-2890000662 | 1Emergency CM Minor Tx GSU | Unclassified | CHANGED OUT NITRGEN BOTTLE [MxOrder - 2002-2890000662 / 1Emergency CM Minor Tx GSU] | FERNANDEZ, GUSTAVO | Maintenance | Lite Truck |  | Lite Truck | Manual | FERNANDEZ, GUSTAVO |  | 2002-06-20 14:26 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2010-1990002491 | 1Emergency CM Minor Tx GSU | Unclassified | 4-23-10 Install grounds on #2 GSU. DBRWA / Absher [MxOrder - 2010-1990002491 / 1Emergency CM Minor Tx GSU] |  | Maintenance | Lite Truck | P1 | Lite Truck | Manual | ALMAND, ROBERT |  | 2010-04-23 14:17 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
1999-2890000195 | 1Emergency CM Minor Tx GSU | Unclassified | 10/7/99, # 2 GSU PLEASE CHANGED OUT BAD FAN MOTOR, BANK # 1, BOTTOM FAN MOTOR 2 MAN JOB, DBRNP 10/12/99 REMOVE MOTOR FOR REPAIR OR REPLACEMENT. DBMGL/DBKDH.10/13/99 REPLACE FAN DBMGL/DBKDH. {MxOrder - 1999-2890000195 / 1Emergency CM Minor Tx GSU} | LUPER, MICHAEL | Maintenance | Shop |  | Lite Truck | Manual |  |  | 1999-10-13 11:25 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 |  | 1999-10-12 13:40 | [5 empty] | No Archive
2000-2890000314 | 1Emergency CM Minor Tx GSU | Unclassified | 5/31/00, HIGH OIL TEMP. ALARM ALL FANS & PUMPS WERE RUNNING PLEASE HAVE PUMP ROTATION ON THE NW. COOLER CHECK OUT BELEIVE IT MAY BE RUNNING BACKWARDS DBRNP 6/2/00 PROBLEM CORRECTED {MxOrder - 2000-2890000314 / 1Emergency CM Minor Tx GSU} | URBANIK, JAMES | Maintenance | Shows - Preview |  | Lite Truck | Manual |  | 2000-06-01 | 2000-06-02 11:44 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-2890000323 | 1Emergency CM Minor Tx GSU | Unclassified | HIGH OIL TEMP ALARM. TEMP HIGH BECAUSE OF LOAD. REMOVED BAD FAN MOTOR ON S.E. COOLER. BOTTOM FAN. NEED TO REPLACE IN A.M, DID NOT HAVE MEGGER TO CHECK MOTOR. LEFT PARTS AT COOLER, OLD MOTOR ON FLOAT IN SHOP, PLEASE HAVE CHECKED OUT. 6/20/00 DBKDH. 06/20/00 INSTALL NEW FAN MOTOR OLD ONE IN SHOP NEEDS REPAIR. DBMGL/DBTGD 6/27/00 if new fan was installed this Mx order is finished and should be closed by light truck Supervisor.dbrsy {MxOrder - 2000-2890000323 / 1Emergency CM Minor Tx GSU} | YOUNG, SCOTT | Maintenance | Shows - Preview |  | Lite Truck | Manual |  | 2000-06-20 | 2000-06-27 16:22 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-2890000382 | 1Emergency CM Minor Tx GSU | Unclassified | 8/24/00, ALARM #2 GSU BIG BEND. FOUND BAD A/C CORD FOR PUMP MOTOR ON BANK # 4 REPLACED CORD, CHECKED OUT OK COMPLETE DBRNP {MxOrder - 2000-2890000382 / 1Emergency CM Minor Tx GSU} | POTTER, RONALD | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 2000-08-24 21:35 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-2980000107 | 1Emergency CM Minor Tx GSU | Unclassified | 1/28/2000..PUT ON UNIT #2 FOR P.R. DISP , CHECKED ALL FANS AND PUMPS..DBCKL {MxOrder - 2000-2980000107 / 1Emergency CM Minor Tx GSU} | LIVINGSTON, CHARLES | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 2000-01-29 06:15 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2001-2980000281 | 1Emergency CM Minor Tx GSU | Unclassified | 9/16/01 FANS ON MAN.AT THIS TIME.... PLANT SAID SECOND BANK DID NOT COME ON WHEN TEMP. GOT ABOVE 85 DEG-C GAUGE NEEDS TO BE CHECKED OUT....DBGSB {MxOrder - 2001-2980000281 / 1Emergency CM Minor Tx GSU} | HALL, EMMETT (CHIP) | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 2001-09-18 07:36 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2003-2980000553 | 1Emergency CM Minor Tx GSU | Unclassified | 8/19/03 NIT. ALARM, PRESS. NORMAL 1600 PSI. RESET AT PANEL OK.....DBGSB UNIT OFF LINE... [MxOrder - 2003-2980000553 / 1Emergency CM Minor Tx GSU] | BUTERA, GASPAR | Maintenance | Lite Truck |  | Lite Truck | Manual | BUTERA, GASPAR |  | 2003-08-19 06:41 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2004-2980000710 | 1Emergency CM Minor Tx GSU | Unclassified | 9/23/04 Called to #2 main trans. to check high oil temp alarm was able to clear alarm . All pumps and fans were running, temp was up due to load. DBDMH. [MxOrder - 2004-2980000710 / 1Emergency CM Minor Tx GSU] | BERRY, STEVE | Maintenance | Lite Truck | P1 | Lite Truck | Manual | HOWARD, DAVID |  | 2004-10-25 09:53 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2009-1960001613 | 1Emergency CM Minor Tx GSU | Unclassified | 4/8/09-Was called to #2-GSU for an alarm. Pressure relief was in. After much checking we found the middle pressure relief to be the one in alarm. We isolated the West & middle P R's and left the East hooked up.We checked the East-PR and it would send the alarm and it also cleared the alarm. Chip Hall and McCatty know about the problem and we can still put the unit on. When the unit comes down again we can get back on top of the Tx and fix the middle pressure relief and rehook all three back up. DBHTB/ DBRWA 4/24/09-Checked out the PR's again and found the West contact to be bad, so changed it out and wired all three back up and sent the alarms and we cleared them. All back normal. DBHTB/ DBRWA 4-25-09 CALLED BACK ON AL. REPLACED 2 WIRES & MID. CONTACTOR CK AL. WE SENT AL. & CLEARED THEM. ALL WORKING DBAXR/ DBRWA [MxOrder - 2009-1960001613 / 1Emergency CM Minor Tx GSU] | MCCATTY, DONALD | Operations | Lite Truck | P3 | Lite Truck | Manual | BELL, HOWARD | 2009-04-08 10:12 | 2009-04-25 17:13 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1970000321 | 1Emergency CM Minor Tx GSU | Unclassified | 2/4/00 JIM OIL PUMP ON WEST COOLER IS LEAKING ON FLANGE WHERE ELECTRIC PLUG PLUGS INTO PUMP MOTOR. APPLIED FIRST STAGE OF LEAK REPAIR. WILL MONITOR 2/17/00JIM CLEANED OIL LEAK STILL LEAKING.----- NORTH EAST OIL PUMP LEAKING AT ELECTRIC PLUG. LOOKS LIKE OIL IS COMING OUT OF WIRE ON PLUG. LEAKS ARE TAGGED WITH METAL TAGS. completed nitrogen leak check.completed regasket oil level gauge and oil temp device winding temp device.oil test k.v. 33k.v. oil temp gauge gasket 3/16 thick outside #2 3/8 inside {MxOrder - 2000-1970000321 / 1Emergency CM Minor Tx GSU} | SMITH, GREGORY | Maintenance | Shows - Preview |  | Lite Truck | Manual |  | 1/1/1800 00:00 | 2001-03-05 07:43 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 |  | 2001-03-01 | 2000-02-22 16:21 |  |  |  |  | No Archive
2000-1970000333 | 1Emergency CM Minor Tx GSU | Unclassified | 2/19/00JIM TX OIL TEMP AND WINDING TEMP GAGES HAVE BEEN BROKEN OFF. LOOKS LIKE SOME STEPPED ON THEM WHILE HANGING GROUNDS. HARD PLASTIC GAGES ARE BROKEN OFF AT BACK OF GAGE . 2-22-00 DBTGD REPLACED WINDING & OIL TEMP. GAUGES TESTED ALARMS & FAN CONTROL JOB COMPLETE./ {MxOrder - 2000-1970000333 / 1Emergency CM Minor Tx GSU} | KELLY, GLENN | Maintenance | Shows - Preview |  | Lite Truck | Manual |  |  | 2000-02-22 16:23 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1970000367 | 1Emergency CM Minor Tx GSU | Unclassified | 5/30/00JIM MIDDLE FAN WEST SIDE HAS GONE BAD ,BEARINGS SOUND LIKE THEY ARE FREEZING UP. REPLACE FAN MOTOR. OLD FAN MOTOR IN SHOP, TAGGED ON SHELF, SEND OUT FOR REPAIR AS NEEDED, 480 VOLT , 3 PHASE -------- AND BACK INTO STOCK THANKS SEND MOTOR OUT FOR REPAIR. TMRGK. {MxOrder - 2000-1970000367 / 1Emergency CM Minor Tx GSU} | YOUNG, SCOTT | Maintenance | Lite Truck |  | Lite Truck | Manual |  | 2000-05-31 | 2000-06-09 17:03 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1970000375 | 1Emergency CM Minor Tx GSU | Unclassified | 6/13/00JIM PALM RIVER HAD NO FLOW ALARM ON TX. FOUND BAD FAN MOTOR. UNPLUGGED COOLER AND PUMP BACK IN SERVICE. WILL REPLACE MOTOR IN AM. PLEASE SUPPLY FAN MOTOR ASAP.replaced 20 foot of cord 3/12 old cord was breidle and cracked, replaced fan motor, MOTOR RAN FOR 2hrs than quit running please replace motor again ---3 PHASE 480VOLT PLEASE TEST RUN IN SHOP IF USED MOTOR PRIOR TO SENDING OUT JOB COMPLETED. TMRGK. {MxOrder - 2000-1970000375 / 1Emergency CM Minor Tx GSU} | KELLY, GLENN | Maintenance | Shows - Preview |  | Lite Truck | Manual |  |  | 2000-06-20 14:20 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2003-1960000941 | 1Emergency CM Minor Tx GSU | Unclassified |  |  | Maintenance | Lite Truck |  | Lite Truck | Manual | BELL, HOWARD |  | 2003-10-09 10:05 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1960000470 | 1Emergency CM Minor Tx GSU | Unclassified | 10/13/00 change out nitrogen bottle. dbmgl {MxOrder - 2000-1960000470 / 1Emergency CM Minor Tx GSU} | LUPER, MICHAEL | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 2000-10-13 11:37 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2002-1960000824 | 1Emergency CM Minor Tx GSU | Unclassified | 11-22-002 During the weekend inspection I replaced the nitrogen bottle. The tx. had zero pressure and the bottle had zero pressure. Alarms were in but it were not reported to substation. Called Mr. Berry and informed him of my findings. McMinn. [MxOrder - 2002-1960000824 / 1Emergency CM Minor Tx GSU] | MCMINN, STEPHEN | Maintenance | Lite Truck |  | Lite Truck | Manual | MCMINN, STEPHEN |  | 2002-11-22 11:30 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2006-1970001338 | 1Emergency CM Minor Tx GSU | Unclassified |  | KING, WILLIAM (BILLY) | Maintenance | Lite Truck | P1 | Lite Truck | Manual | KING, WILLIAM (BILLY) |  | 2006-02-15 13:06 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2006-1970001358 | 1Emergency CM Minor Tx GSU | Unclassified |  | KING, WILLIAM (BILLY) | Maintenance | Lite Truck | P1 | Lite Truck | Manual | KING, WILLIAM (BILLY) |  | 2006-04-13 11:34 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2008-1970001657 | 1Emergency CM Minor Tx GSU | Unclassified |  | KING, WILLIAM (BILLY) | Maintenance | Lite Truck | P1 | Lite Truck | Manual | KING, WILLIAM (BILLY) |  | 2008-04-02 12:16 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | 902542 | [6 empty] | No Archive
2008-1970001693 | 1Emergency CM Minor Tx GSU | Unclassified |  | KING, WILLIAM (BILLY) | Maintenance | Lite Truck | P1 | Lite Truck | Manual | KING, WILLIAM (BILLY) |  | 2008-05-22 12:40 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2008-1970001695 | 1Emergency CM Minor Tx GSU | Unclassified |  | KING, WILLIAM (BILLY) | Maintenance | Lite Truck | P1 | Lite Truck | Manual | KING, WILLIAM (BILLY) |  | 2008-06-02 13:40 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | 916171 | [6 empty] | No Archive
2008-1970001704 | 1Emergency CM Minor Tx GSU | Unclassified |  | KING, WILLIAM (BILLY) | Maintenance | Lite Truck | P1 | Lite Truck | Manual | KING, WILLIAM (BILLY) |  | 2008-06-12 12:23 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2008-1970001734 | 1Emergency CM Minor Tx GSU | Unclassified |  | KING, WILLIAM (BILLY) | Maintenance | Lite Truck | P1 | Lite Truck | Manual | KING, WILLIAM (BILLY) |  | 2008-08-19 11:14 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2007-1990001815 | 1Emergency CM Minor Tx GSU | Unclassified | Bad fan west bank, middle fan. Will replace Monday. Two man job.. 2-24-07 DBCWB. 2/266/07---Replaced bad fan motor, this date.--- GF/ RBC [MxOrder - 2007-1990001815 / 1Emergency CM Minor Tx GSU] | MCCATTY, DONALD | Maintenance | Lite Truck | P1 | Lite Truck | Manual | BLEDSOE, CHARLES (WAYNE) |  | 2007-02-26 11:43 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2004-1990001332 | 1Emergency CM Minor Tx GSU | Unclassified |  | BLEDSOE, CHARLES (WAYNE) | Maintenance | Lite Truck | P1 | Lite Truck | Manual | BLEDSOE, CHARLES (WAYNE) |  | 2004-11-06 07:46 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2008-1980001926 | 1Emergency CM Minor Tx GSU | Unclassified | 7/9/08 HI OIL TEMP. ALARM. ALL FANS & PUMPS RUNNING. OIL TEMP. @ 93 DEG. C WINDING TEMP. @ 120 DEG. C. CALLED D. MCCATTY & E. ATIENZA. PLANT TO BACK DOWN ON TX. AFTER ONE HOUR TEMP. HAD DROPPED 2 DEG. PLANT OPERATOR TO MONITOR. DBGHP 1/6/09 ALL COOLERS AND PMPS ARE BEING REPLACED OR REGASKETED. THIS WILL FIX THIS PROBLEM. [MxOrder - 2008-1980001926 / 1Emergency CM Minor Tx GSU] | MCCATTY, DONALD | Maintenance | Lite Truck | P1 | Lite Truck | Manual | PAUL, GILBERT |  | 2009-01-06 16:30 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2008-1980001954 | 1Emergency CM Minor Tx GSU | Unclassified | 8/4/08 P.R. REPORTED THAT BIG BEND CONTROL ROOM HAD A LOW OIL LEVEL ALARM ON #2 GSU. CHECKED OIL LEVEL GAUGE OIL LEVEL NORMAL. OIL LEVEL ALARM WAS IN RESET ALARM. ALL CLEAR. DBGHP [MxOrder - 2008-1980001954 / 1Emergency CM Minor Tx GSU] | PAUL, GILBERT | Maintenance | Lite Truck | P1 | Lite Truck | Manual | PAUL, GILBERT |  | 2008-08-04 16:29 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2008-1980001962 | 1Emergency CM Minor Tx GSU | Unclassified | 8/20/08 LOW NIT. PRESS. ALARM. FOUND LOW PRESS. GAUGE @ 0 PSI. BOTTLE HAD 2200 PSI ON IT. AJUSTED LOW PRESS. REGULATOR. REG. IS MARKED IF IT IS DESIRED TO PUT BACK TO ORIGINAL SETTING. TURN OUT TO LINE UP MARKS TO PUT BACK TO ORIGNAL SETTING.. LOW PRESS. GAUGE @ .4 PSI. ALARM CLEARED. DBGHP 10-15-08 -- WWK -- TX normal @ this time -- closed MX -- [MxOrder - 2008-1980001962 / 1Emergency CM Minor Tx GSU] | MCCATTY, DONALD | Maintenance | Lite Truck | P2 | Lite Truck | Manual | PAUL, GILBERT |  | 2008-10-15 05:02 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2011-1980002623 | 1Emergency CM Minor Tx GSU | Unclassified | 5/16/11 GROUND BIG BEND #2 GSU. DBGHP DBZWR [MxOrder - 2011-1980002623 / 1Emergency CM Minor Tx GSU] | COLEMAN, STEVE | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | PAUL, GILBERT |  | 2011-05-19 06:45 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2001-1990000578 | 1Emergency CM Minor Tx GSU | Unclassified | Low oil flow #1 cooler alarm. Reset OK. 9-22-01 DBCWB . {MxOrder - 2001-1990000578 / 1Emergency CM Minor Tx GSU} | BLEDSOE, CHARLES (WAYNE) | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 2001-09-22 08:34 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2002-1990000696 | 1Emergency CM Minor Tx GSU | Unclassified |  | BRYAN, DAVID | Maintenance | Lite Truck |  | Lite Truck | Manual | BRYAN, DAVID |  | 2002-06-22 04:30 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2003-1980000861 | 1Emergency CM Minor Tx GSU | Unclassified | 1/17/03 #5 COOLER TOP FAN KEEPS TRIPPING BREACKER. UNPLUGGED FAN WILL REMOVE AND REPLACE 1/20 PLEASE ORDER FAN MOTOR AND STAGE. [MxOrder - 2003-1980000861 / 1Emergency CM Minor Tx GSU] | URBANIK, JAMES | Maintenance | Lite Truck |  | Lite Truck | Manual | URBANIK, JAMES |  | 2003-01-24 08:07 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2003-1980000929 | 1Emergency CM Minor Tx GSU | Unclassified | 6/11/03JIM HAD TWO BAD FANS. REMOVED FOR REPAIR, IN SHOP ON FLOAT. PARTS HDR DV56 440/480 VOLT 870 RPM 3 PH 2.7 AMP ID# P18G6686A ORDERED MOTORS ON PHONE FROM JOE L 6/11/03 TO BE STAGED IN SHOP IN AM.-- WIRED AND PLACED BOTH MOTOR IN COOLER. NEED 45 FT 3/12C S/O TO REPLACE OLD CABLES. ALSO NEED KEYS AND CONNECTION BOX FITTINGS FOR BOTH MOTORS. 6/25/03 DBKDH-- COMPLETED FAN MOTOR INSTALLATION.6/26/03 DBKDH [MxOrder - 2003-1980000929 / 1Emergency CM Minor Tx GSU] | HARRELL, KENNETH | Maintenance | Contractor |  | Lite Truck | Manual | URBANIK, JAMES |  | 2003-06-26 19:29 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2003-1980000950 | 1Emergency CM Minor Tx GSU | Unclassified | 8/8/03JIM CHANGE OUT NITROGEN BOTTLE [MxOrder - 2003-1980000950 / 1Emergency CM Minor Tx GSU] | URBANIK, JAMES | Maintenance | Lite Truck |  | Lite Truck | Manual | URBANIK, JAMES |  | 2003-08-08 17:43 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2001-1910000201 | 1Emergency CM Minor Tx GSU | Unclassified | FAN MOTOR ON #3 COOLER OF #2 GSU HAS SHORTED. CHECKED CABLE AND PLUG TO BE GOOD. NEED TO HAVE MOTOR CHANGED OUT IN A.M. UNPLUGGED CABLE AND TAGGED. WILL NEED HELP WITH CHANGE OUT. 6/20/01 DBKDH 6/21/2001 REPLACED FAN MOTOR, RUNNING OK WORKED WITH B. KING JOB COMPLETE............. {MxOrder - 2001-1910000201 / 1Emergency CM Minor Tx GSU} | KELLY, GLENN | Maintenance | Fan Motor |  | Lite Truck | Manual |  |  | 2001-06-21 11:21 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2020-3000082266 | 1Emergency CM Minor Tx GSU | Unclassified | P.R. had pressure/vac alarm c/o bottles on #2 12/2/20 Main [MxOrder - 2020-3000082266 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective |  | Lite Truck | Manual | MAIN, JUSTIN |  | 2020-12-02 13:36 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 188 | [7 empty] | No Archive
1999-1920000210 | 1Emergency CM Minor Tx GSU | Unclassified | CHANGED OUT NITROGEN BOTTLE. 9/12/99 DBKDH {MxOrder - 1999-1920000210 / 1Emergency CM Minor Tx GSU} | HARRELL, KENNETH | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 1999-09-12 09:30 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2009-1920002169 | 1Emergency CM Minor Tx GSU | Unclassified | 2-28-09 CIRCUIT BREAKER #1 FOR FANS & PUMPS ON #2 GSU @ BIG BEND NEEDS TO BE REPLACED. UNIT IS DOWN. BREAKER INFO ITE 480 VOLT 30 AMP CAT# EH3-3030V OR CULTER-HAMMER 30 AMP 3 POLE CAT# EHD 3030 STYLE # 6638C90G87 DBAXR 3/3/09 CH/O CB as per MX. DBMHC [MxOrder - 2009-1920002169 / 1Emergency CM Minor Tx GSU] | MCCATTY, DONALD | Maintenance | Lite Truck | P2 | Lite Truck | Manual | ROCAMORA, ALBERT |  | 2009-03-03 18:57 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2009-1920002190 | 1Emergency CM Minor Tx GSU | Unclassified | 4-18-09 CALLED ON OIL TEMP. AL. FOUND OIL @ 75 & WINDING @ 88 NO AL. IN ON ANNUCIATOR IN CABINET. & CONTROL ROOM DIDN'T HAVE AL. I TALKED WITH K.HERRELL & PLANT OPER. & LEFT FANS ON MANUAL TILL GAUGE CAN BE LOOKED AT. DBAXR CALLED BACK OUT ON OIL TEMP. TALKED WITH K. HERRALL OIL & WINDING TEMP. WERE GOOD. C. HALL WILL GET WITH RTU ON MON. DBAXR 5/1/09 SENT TO BB #2GSU FOR TEMP ALM. OIL DRAG AND ACT 80C, WINDING DRAG AND ACT. 90C. BB CONTROL RM DOESN T HAVE THIS ALM. I SPOKE WITH C. HALL THIS IS A BOGUS ALM. CHIP SAID HE WILL SPEAK TO RTU AGAIN.DBMHC 08-29-09 PR reported hi / temp. liquid alarm. I found no alarms in cabinet. Actual liquid temp :75c Actual winding temp:90c Recommend checking liq. and wind. connection points to be sure they have not been rolled. DBJVM 09-04-09 Re- check alarms, found conditions normal at TX. However, PR is still showing alarms on their display. No alarms in BB control room. DBJVM 9/23/09 AS PER J URBANIK WE HAVE PROVIDED THE PLANT ELEC. ENGINEER WITH THE RELAY NESSISARY TO RESOVE THIS PROBLEM ON THEIR END. DBMHC [M xOrder - 2009-1920002190 / 1Emergency CM Minor Tx GSU] | HARRELL, KENNETH | Maintenance | Lite Truck | P1 | Lite Truck | Manual | ROCAMORA, ALBERT |  | 2009-09-23 12:14 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2009-1920002229 | 1Emergency CM Minor Tx GSU | Unclassified | 5-28-09 NOTHING IN CASCADE FOR # 2 B.S.S. CALLED FOR LOSS OF AC & COOLER AL. FOUND FANS ON MANUAL. TEMP. WAS 54C. FANS COME IN AT 75 C. PUT BACK ON AUTO. CK. IN CONTROL ROOM NO AL. DBAXR 6/7/9 I was called to BB for same alm. The TX temp was 55 c this is not hi enough to made the fans come on. PR. screan showed 90c. to clear the alm I put the fans on manual . as the temp droped the alm cleared.. DBMHC I got called away for another emerg. when I came back this TX was in alm for lo inertaire. loss of fan bk. ac. and a loss of #1 fan bk. The fan bk were still running and I still had both ac s. but the ac swap over had sw to e source. I found a ph monitor tripped on the back of the panel and re set it. this made the swap over sw. and cleared all the alms. at BB. PR. still had a general alm in which even after much effort I was unable to locate.I have been having trouble with alms at PR not clearing even after the problem has been resolved . LAMAR said he would have rtu look at it tonigth when the unit came dn. DBMHC [MxOrder - 2009-1920002229 / 1Emergency CM Minor Tx GSU] |  | Maintenance | Lite Truck | P1 | Lite Truck | Manual | ROCAMORA, ALBERT |  | 2009-07-14 18:22 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2010-1920002431 | 1Emergency CM Minor Tx GSU | Unclassified | 9-10-10 REMOVE GROUNDS #2 MAIN DBAXR [MxOrder - 2010-1920002431 / 1Emergency CM Minor Tx GSU] |  | Maintenance | Lite Truck | P1 | Lite Truck | Manual | ROCAMORA, ALBERT |  | 2010-09-14 21:09 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2011-1920002494 | 1Emergency CM Minor Tx GSU | Unclassified | 2-17-11 C/O NIT. CYL. & PUT A SPARE IN RACK. TX USED 600 PSI IN 45 MIN. REMOVED 5 CYL. FROM OTHER TX. THAT WERE MT. & TIED TO SIDE OF TX.s SENT BACK TO YARD WITH C. CREWS DBAXR 5-13-11 LOW PRESS. AL. FOUND REG. BACKED COMP. OUT. READJUSTED & CLEARED AL. DBAXR 8-5-11 C/O NIT. CYL. PLANT DID NOT GET AL. TROUBLE SHOOTING FOUND WE HAD AL. IN CABINET BUT NOT IN CONTROL ROOM. GOT WITH TOM BLAIR HE WAS GETTING AL. BUT NOT ON SCREEN. HE WILL LOOK IN TO IT. ROCK [MxOrder - 2011-1920002494 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Lite Truck | Manual | ROCAMORA, ALBERT |  | 2011-10-10 10:51 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2011-1920002525 | 1Emergency CM Minor Tx GSU | Unclassified | 4-12-11 NEED TO REPLACE FAN MOTOR WEST MID. DBAXR [MxOrder - 2011-1920002525 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P2 | Lite Truck | Manual | ROCAMORA, ALBERT |  | 2011-05-04 09:00 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1930000554 | 1Emergency CM Minor Tx GSU | Unclassified | 10/21/00--I removed a bad fan from the north , center cooler , center fan. The motor will be on a float in the shop and tagged. Mr Mecleod is going to call out a parts man and have the replacement fan installed tommorow.-Theree is a part number on the motor-651-0807-16A4Westinghouse 184T-230/460--870---dbdkb---10/22/00--We have completed changing out the bad fan motor, checked the rotation and checked to make sure there were no alarms.--dbdkb {MxOrder - 2000-1930000554 / 1Emergency CM Minor Tx GSU} | BRYAN, DAVID | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 2000-10-22 13:00 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2001-1930000816 | 1Emergency CM Minor Tx GSU | Unclassified | 10/21/01--The fan motor is bad and needs to be changed out ASAP. I notified the on call foreman. It is the center fan on cooler #6 and its power cord is unplugged at the tx. It is rai\ning hard and as per Mr Wirth , I did not remove fan ---dbdkb 1O/23 DBTGD REPLACED FAN MOTOR ,RUNNING OK JOB COMPLETE.......... {MxOrder - 2001-1930000816 / 1Emergency CM Minor Tx GSU} | DIETZ, TERRY | Maintenance | Shows - Preview |  | Lite Truck | Manual |  |  | 2001-10-23 13:06 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2006-1950001589 | 1Emergency CM Minor Tx GSU | Unclassified | 7/29/06 HIGH OIL TEMP. ALARM @ 90C . ALL FANS RUNNING. DBCEC [MxOrder - 2006-1950001589 / 1Emergency CM Minor Tx GSU] |  | Maintenance | Lite Truck | P1 | Lite Truck | Manual | CROWELL, CARL |  | 2006-07-29 18:21 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2011-1820000229 | 1Emergency CM Minor Tx GSU | Unclassified | #2 Unit tripped on relay lockouts.Plant found damage to isophase of GSU above A-phase bushing and inside plant isophase C-phase braided bus llinks(shunts).TCG test of GSU was 0.05,good. ---2-8-11--doble test TX. found HO is bad, everything else OK--DBMWV----2-9-11--replace HO bushing---DBMWV [MxOrder - 2011-1820000229 / 1Emergency CM Minor Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Maintenance 4 Man Crew | Manual | VAN GALDER, MARK |  | 2011-10-10 10:54 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
1999-1960000253 | 1Emergency CM Minor Tx GSU | Unclassified | 10/19/99 CHANGE OUT NITROGEN BOTTLE DBMGL. {MxOrder - 1999-1960000253 / 1Emergency CM Minor Tx GSU} | LUPER, MICHAEL | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 1999-10-19 13:54 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2009-1940002359 | 1Emergency CM Minor Tx GSU | Unclassified | 04/01/09---We were sent to Big Bend to trouble shoot one of the new cooler fans that was not running (reported by the plant). There was a "DO NOT ENTER" barricade around the tx which was tagged with a red tag. We were unable to get permission to enter the area.----dbdkb 4/13/09 D. BRYAN and Myself comp. this MX the next day under a differant MX. DBMHC [MxOrder - 2009-1940002359 / 1Emergency CM Minor Tx GSU] | MCCATTY, DONALD | Maintenance | Lite Truck | P1 | Lite Truck | Manual | BRYAN, DAVID |  | 2009-04-13 18:23 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2002-1920000751 | 1Emergency CM Minor Tx GSU | Unclassified | 12/02/02 DBTGD ALARM , FOUND ( 0 ) PSI OF NIT. REPLACED NIT. BOTTLE, CHECKED FOR LEAK,S FOUND NONE,----- UNIT OFF LINE.....@45 DEG. [MxOrder - 2002-1920000751 / 1Emergency CM Minor Tx GSU] | DIETZ, TERRY | Maintenance | Lite Truck |  | Lite Truck | Manual | DIETZ, TERRY |  | 2002-12-02 09:00 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2003-1920000931 | 1Emergency CM Minor Tx GSU | Unclassified | 10/09/03 Low nitrogen bottle pressure, 450 psi. I attempted to change the bottle but the spare bottles have the wrong fittings Left message for Steve Berry about this problem. DBRWA [MxOrder - 2003-1920000931 / 1Emergency CM Minor Tx GSU] |  | Maintenance | Lite Truck |  | Lite Truck | Manual | ALMAND, ROBERT |  | 2003-10-09 04:12 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2004-1920001024 | 1Emergency CM Minor Tx GSU | Unclassified | 3/31/04 Oil flow alarm on cooler group 2. Found all fans and pumps running and oil flow gauges showing oil flow. Tried to reset alarm, would not clear. Tapped on all oil flow gauges and alarm reset. Possible dirty contact in one of the oil flow gauges. DBRWA [MxOrder - 2004-1920001024 / 1Emergency CM Minor Tx GSU] |  | Maintenance | Lite Truck |  | Lite Truck | Manual | ALMAND, ROBERT |  | 2004-03-31 07:40 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2007-1930001947 | 1Emergency CM Minor Tx GSU | Unclassified | 5/15/07 OIL IS LEAKING FROM THE SAMPLING VALVE. CLEANED UP THE OIL AND REDID THE FITTINGS. PLEASE RECHECK IN A FEW DAYS. DBMHC Stopped leaking. 5-18-07 DBCWB . [MxOrder - 2007-1930001947 / 1Emergency CM Minor Tx GSU] | BLEDSOE, CHARLES (WAYNE) | Maintenance | Lite Truck | P2 | Lite Truck | Manual | CHICO, MICHAEL |  | 2007-05-18 09:54 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2007-1930001955 | 1Emergency CM Minor Tx GSU | Unclassified | 6/2/07 #1 GSU FANs IN ALM. AN EMC CB IN THE PLANT HAD FAULTED AND FAILED . AFTER THE PLANT RESTORED POWER SOME OF THE FANS AND PUMPS STAYED OFF. I RESET THE CBs AND RESET THE ALMS. ALL CLEARED. DBMHC. [MxOrder - 2007-1930001955 / 1Emergency CM Minor Tx GSU] | MCCATTY, DONALD | Maintenance | Lite Truck | P1 | Lite Truck | Manual | CHICO, MICHAEL |  | 2007-06-02 12:09 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2007-1930002021 | 1Emergency CM Minor Tx GSU | Unclassified | 9/24/07 LO NITROGEN ALM @ # 2 GSU BB. CH/O BOTTLE CLEARED ALM. DBMHC [MxOrder - 2007-1930002021 / 1Emergency CM Minor Tx GSU] | URBANIK, JAMES | Maintenance | Lite Truck | P1 | Lite Truck | Manual | CHICO, MICHAEL |  | 2007-09-24 03:14 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | 859207 | [6 empty] | No Archive
1999-1940000116 | 1Emergency CM Minor Tx GSU | Unclassified | UNIT 2 COOLER FAILURE. FOUND BURNT JUMPER ON #2 FAN BREAKER. REPLACED JUMPER, AND MONITORED FANS. OK. 4/27/99 KDH {MxOrder - 1999-1940000116 / 1Emergency CM Minor Tx GSU} | HARRELL, KENNETH | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 1999-04-27 09:37 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 |  | 1999-04-27 09:36 | [5 empty] | No Archive
1999-1940000117 | 1Emergency CM Minor Tx GSU | Unclassified | UNIT 2 GSU COOLER FAILURE. FOUND #2 FAN CB BAD. REPLACED CB , HAD TO RETROFIT NEW CB TO BE ABLE TO INSTALL. 4/28/99 KDH---ML HAD TROUBLE FINDING PARTS TO INSTALL CB. {MxOrder - 1999-1940000117 / 1Emergency CM Minor Tx GSU} | HARRELL, KENNETH | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 1999-04-28 12:52 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 |  | 1999-04-28 12:49 | [5 empty] | No Archive
1999-1940000162 | 1Emergency CM Minor Tx GSU | Unclassified | CHANGED OUT NITROGEN BOTTLE AND CHECKED FOR LEAKS AROUND REGULATOR AND GAS LINES. FOUND NONE. TX MX'D FOR LEAK CHECK ALREADY. 6/16/99 DBKDH {MxOrder - 1999-1940000162 / 1Emergency CM Minor Tx GSU} | HARRELL, KENNETH | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 1999-06-16 13:25 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1940000324 | 1Emergency CM Minor Tx GSU | Unclassified | 07-09-00--WWK--Chg/out M-T Nit bottle-- {MxOrder - 2000-1940000324 / 1Emergency CM Minor Tx GSU} | KING, WILLIAM (BILLY) | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 2000-07-09 07:35 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1940000331 | 1Emergency CM Minor Tx GSU | Unclassified | 07-17-00--WWK-- Put a 55 gallon "used oil" drum from the plant, to drain 5 gallon buckets located under radiator oil pumps, and drained all the 5 gallon buckets, arranged for the plant to monitor same -- also fixed flat tires on nitrogen bottle cart, located @ #2 GSU-- {MxOrder - 2000-1940000331 / 1Emergency CM Minor Tx GSU} | KING, WILLIAM (BILLY) | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 2000-07-17 11:51 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1940000341 | 1Emergency CM Minor Tx GSU | Unclassified | 07-23-00--WWK-- Chg - out Nitrogen bottle {MxOrder - 2000-1940000341 / 1Emergency CM Minor Tx GSU} | KING, WILLIAM (BILLY) | Maintenance | Lite Truck |  | Lite Truck | Manual |  |  | 2000-07-23 11:01 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2006-1940001426 | 1Emergency CM Minor Tx GSU | Unclassified | 3/21/06 Found themals on 2,4 & 6 coolers tripped and reset, watched a short time and thermals held. DBDMH. 3/22/06 If coolers trip again voltage needs to be checked on P&E feeds to see if voltage is up,voltage was at 450 VAC and all the legs at about 16 to 18 amps. Also heater fuses have been pulled due to high heat in cabinet.DBDMH. 3/31/06 KENNY THE FANS HAVE BEEN RUNNING SINCE DAVE RESET THEM .I CHECKED AS YOU ASKED EVERYTHING NORMAL. VOLTAGE AT THE BOTTOM OF BREAKERS 2,4, AND 6. X TO Y 451, Y TO Z 449, X TO Z 449. AMPS 2 -X 14.3 ,Y 14 , Z 14.5. 4 -X 14.2 ,Y 13.7 , Z 14.2. 6 X 15.3 , Y 14.7 , Z 15.6. AMPS AT FEED FOR 2 -45, 4-43.5, 6-44.3. AMPS AT FEED FOR 1-43.4 , 3 -44 , 5-43.5.GEF --- VOLTAGE FROM PLANT TO TX WAS FOUND TO BE LOW. PLANT CORRECTING. DBKDH [MxOrder - 2006-1940001426 / 1Emergency CM Minor Tx GSU] | HARRELL, KENNETH | Maintenance | Lite Truck | P2 | Lite Truck | Manual | HOWARD, DAVID |  | 2006-04-21 14:51 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2006-1940001432 | 1Emergency CM Minor Tx GSU | Unclassified | 3/26/06 Changed out low nitrogen bottle to clear alarm.DBDMH. [MxOrder - 2006-1940001432 / 1Emergency CM Minor Tx GSU] | HOWARD, DAVID | Maintenance | Lite Truck | P1 | Lite Truck | Manual | HOWARD, DAVID | 2006-03-26 01:52 | 2006-03-26 02:55 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2006-1940001453 | 1Emergency CM Minor Tx GSU | Unclassified | 5/10/06 #2 contacter had tripped reset and watched for 30 minutes.DBDMH. [MxOrder - 2006-1940001453 / 1Emergency CM Minor Tx GSU] |  | Maintenance | Lite Truck | P3 | Lite Truck | Manual | HOWARD, DAVID |  | 2006-05-10 02:46 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2006-1940001467 | 1Emergency CM Minor Tx GSU | Unclassified | 6/5/06 Checked winding & oil temp. after radiators were washed , found oil at 68 & drag at 70 winding at 85 & drag at 89 this was at noon. DBDMH. 6/6/06 Checked temp. of oil & winding,oil was 72 and winding was 91 at 1500 PM. DBDMH. [MxOrder - 2006-1940001467 / 1Emergency CM Minor Tx GSU] | HARRELL, KENNETH | Maintenance | Lite Truck | P3 | Lite Truck | Manual | HOWARD, DAVID |  | 2006-06-06 07:14 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2008-1940002011 | 1Emergency CM Minor Tx GSU | Unclassified | 02/09/08----The plant called me out for a cooler failure alarm and an oil flow alarm. CB was tripped on cooler #6. I found the bearings on the center fan motor were frozen up. I unplugged the fan and reset the CB. The CB stayed in and the remaining two fans ran as well as the oil pump. The alarms cleared. I notified the on call supervisor. He called out a parts man and another Jouneyman. We removed the old motor but the replacementt part listed for this tx was not correct and the base was to wide. The parts man had to locate the correct motor and deliver it. We installed the new fan motor and cleared the alarms.-----dbdkb dbaxr [MxOrder - 2008-1940002011 / 1Emergency CM Minor Tx GSU] | MCCATTY, DONALD | Maintenance | Lite Truck | P1 | Lite Truck | Manual | BRYAN, DAVID |  | 2008-02-10 03:51 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2007-1820000091 | 1Emergency CM Tx Cooler Washing Tx GSU | Unclassified |  |  | Maintenance | Maintenance 2 Man Crew | P1 | Maintenance 2 Man Crew | Manual | RAULERSON, GARY |  | 2008-07-09 17:41 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | 824636 | [6 empty] | No Archive
2000-1920000352 | 1Emergency CM Operations Storm Tx GSU | Unclassified | 6/19/2000 DBTGD FOUND BOTTLE 100 PSI REPLACED BOTTLE CLEARED ALARM. 5 PSI LOW SIDE. 6/19/2000 TGD ALARM ON NIT. SYS.100 PSI ON BOTTLEUNIT USED 2100 PSI IN 8 HOURS CHECKED FOR LEAKS, FOUND NONE REGULATOR WAS CRANKED DOWN TIGHT PUTTING APROX. 9 LLBS OF PRESSURE GOING INTO TX, RESET TO APROX. 3.5 I WILL LEAVE MX ORDER OPEN ,IN CASE THIS DOES NOT FIX THE PROLBLEM. 6/20/2000 TGD CHECKED NIT. TODAY UNIT WAS NORMAL .CLOSING MXORDER. {MxOrder - 2000-1920000352 / 1Emergency CM Operations Storm Tx GSU} | DIETZ, TERRY | Station | Shop |  | Lite Truck | Manual |  |  | 2000-06-20 10:54 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2016-3000022569 | 1Emergency CM Operations Storm Tx GSU | Unclassified | 12-23-16 sc gsu #2 bank 2 coil burned up replaced coil and cleaned contacts [MxOrder - 2016-3000022569 / 1Emergency CM Operations Storm Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P3 | Lite Truck | Manual | COLEMAN, STEVE |  | 2018-02-13 09:34 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 22715 | [7 empty] | No Archive
2013-3000110086 | 1Emergency CM Maintenance Storm Tx GSU | Unclassified | #2 GSU TX HAS A BLOW CONTROL POWER TX IN THE CONTROL CAB NEEDS TO BE CHANGE OUT NEXT OUTAGE.....ASMDM....2/10/13.CPT TXs WERE PEPLACE 2/10/13. SEE ASSOCIATED W/O IN CASCADE. DK MCCATTY. [MxOrder - 2013-3000110086 / 1Emergency CM Maintenance Storm Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | MONTGOMERY, MICHAEL | 2013-02-10 16:27 | 2014-09-18 13:37 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2014-3000160141 | 1Emergency CM Operations Tx GSU | Unclassified | 12/7/14 Call out, loss of ac power alarm. Plant said they reset alarm a couple of times & it would come back in & then would not reset. All fans & pumps are running & breakers good, ETM has power & good. Top oil temp. 74*c & max is 88*c, windings temp. 89*c & max is 104*c, below alarm points. I reset alarm & stood by for 1 hour to see if alarm comes back in, no alarm.....ABSHER [MxOrder - 2014-3000160141 / 1Emergency CM Operations Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P1 | Lite Truck | Manual | ABSHER, LARRY |  | 2015-06-02 09:16 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000040422 | 1Emergency CM Operations Tx GSU | Unclassified | 7\30\12 ground down #2 unit.abzwr [MxOrder - 2012-3000040422 / 1Emergency CM Operations Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | RAY, ZACHARY |  | 2012-07-30 13:00 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2014-3000021000 | 1Emergency CM Operations Tx GSU | Unclassified | 5-5-14 dbrsc bad fan motor on bank 6 top fan motor [MxOrder - 2014-3000021000 / 1Emergency CM Operations Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P1 | Lite Truck | Manual | COLEMAN, STEVE |  | 2014-05-06 12:35 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2011-3000040158 | 1Emergency CM Operations Tx GSU | Unclassified | 12/1/11 #2 GSU ALARM COOLER FAILURE.WHE I OPENED CONTROL CABINET DOOR SMOKE CAME ROLLING OUT.KILLED ALL BREAKERS INVESTIGATED AND FOUND BURNEDUP COIL ON #2 BANK COOLERS.REPLACED BURNED UP CONTACTOR COIL AND PUT BACK IN SERVICE AND CHECKED OPERATION OF ALL THE FANS AND PUMPS FOR ANY OTHER PROBLEMS.CLEARED ALL ALARMS.ABZWR [MxOrder - 2011-3000040158 / 1Emergency CM Operations Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | RAY, ZACHARY |  | 2011-12-01 23:14 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000020290 | 1Emergency CM Operations Tx GSU | Unclassified | 8-14-12 dbrsc bad fan motor on # 2 bank D 0019150 [MxOrder - 2012-3000020290 / 1Emergency CM Operations Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | COLEMAN, STEVE |  | 2012-08-15 16:09 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000000129 | 1Emergency CM Operations Tx GSU | Unclassified | 10-9-12 Call-out Big Bend #2 GSU-- Loss of power alarm.Alarm was toggling in and out. Found partially blown fuse in undervoltage relay 27-1 control circuit (Fu-1). Could not determine what size fuse to use. However I replaced bad fuse with a 10amp fuse. NOTE: Other fuse for relay 27-2 also needs to be replaced. ABJVM [MxOrder - 2012-3000000129 / 1Emergency CM Operations Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Maintenance 1 Man Crew | Manual | MCCRAY, JOEL |  | 2013-01-24 18:19 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000020160 | 1Emergency CM Operations Tx GSU | Unclassified | 3-18-12 dbrsc nit alarm on #2 gsu turn on bottle cleared alarm [MxOrder - 2012-3000020160 / 1Emergency CM Operations Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | COLEMAN, STEVE |  | 2012-03-18 14:56 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2016-3000022312 | 1Emergency CM Operations Tx GSU | Unclassified | 6-23-16 sc fans quit working on tx plant had a ground on there water dayluges system got fans back on after they lifted wires in there panel [MxOrder - 2016-3000022312 / 1Emergency CM Operations Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective |  | Lite Truck | Manual | COLEMAN, STEVE |  | 2016-06-23 15:01 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 8161 | [7 empty] | No Archive
2016-3000022343 | 1Emergency CM Operations Tx GSU | Unclassified | 7-6-16 sc tx running hot pumps and fans running tom blair had plat take off some of the vars tx cooled down told mccatty rad need to be pressure washed 12-22-16 rad has been cleaned [MxOrder - 2016-3000022343 / 1Emergency CM Operations Tx GSU] | DUKES, JAMES | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P3 | Lite Truck | Manual | COLEMAN, STEVE |  | 2016-12-23 12:08 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 11409 | [7 empty] | No Archive
2012-3000090033 | 1Emergency CM Operations Tx GSU | Unclassified | 5/4/12 Called out for a temp. alm fail. due to the sensitivity of the nerc rules rather than have me reboot it and chance lost info. We opted to have the relay people look at it in the am. I turned off the alm in the TX cabinet. as per J.Urbanik. DBMHC 11/9/12 CALLED OUT FOR #2 GSU ETM ALARM, UNIT TRIPPED OFF LINE , ONE PUMPS WAS NOT RUNNING & FANS WAS RUNNING. RESET CB & CHECKED ETM FUSES & VOLTAGE, PUMP STARTED UP, & ALARM CLEARED.....ABSHER 18 oct 2013 -- called out for #2 gsu etm failure alarm. unit 2 is off line. etm alarm would not clear. all fans and pumps are working fine. urbanik notified and said he will pass it on to kiepke to have the etm checked out. rhodes [MxOrder - 2012-3000090033 / 1Emergency CM Operations Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | CHICO, MICHAEL |  | 2016-01-08 09:58 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 5887 | [7 empty] | No Archive
2019-3000082157 | 1Emergency CM Operations Tx GSU | Unclassified | #2GSU Control Room Called Palm River Middel Pump Was Not Running. Bank #2 Was Running,Middel Pump Runs Only When#1 Kicks In. All Pumps & Fans Are Working. ROCK [MxOrder - 2019-3000082157 / 1Emergency CM Operations Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P1 | Lite Truck | Manual | ROCAMORA, ALBERT | 2019-12-05 09:33 | 2019-12-05 13:25 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 57386 | [7 empty] | No Archive
2001-1920000490 | 1Emergency CM Operations Tx GSU | Unclassified | . 4/02/2001 DBTGD REMOVED FAN MOTOR ON BANK #5 NEED REPLACEMENT MOTOR & BAD MOTOR REPAIRED & PUT INTO STOCK...... RELIANCE 3 PHASE 440 VAC FRAME 184T TYPE P 1 HP 870 RPM. ORDERED MOTOR WITH TED PERRY. 4/10/2001 DBTGD INSTALLED NEW FAN M0T0R , TEST RAN OK. JOB COMPLETE.......... {MxOrder - 2001-1920000490 / 1Emergency CM Operations Tx GSU} | DIETZ, TERRY | Operations | Fan Motor |  | Lite Truck | Manual |  |  | 2001-04-10 10:37 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2001-1920000521 | 1Emergency CM Operations Tx GSU | Unclassified | . 6/01/01 DBTGD FOUND WINDING TEMP. GAUGE BROKEN, SOME ONE USED IT FOR A STEP. NEED,S REPLACED A.S.A.P. COVERED WITH PLASTIC, FAN,S ARE ON MANUAL. WIND. UNIT IS THE OLD STYLE PENNSYLVANIA 0 TO 180 DEG. WITH APPROX. 4 FT. OF CORD. 6/05/2001 DBTGD WORKED WITH D. NELSON ,INSTALLED NEW GAUGE, TESTED OK JOB COMPLETE............... {MxOrder - 2001-1920000521 / 1Emergency CM Operations Tx GSU} | DIETZ, TERRY | Operations | Shows - Preview |  | Lite Truck | Manual |  |  | 2001-06-05 09:04 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2001-1920000586 | 1Emergency CM Operations Tx GSU | Unclassified | 10/19/01 DBTGD REPLACED NIT BOTTLE, CHECKED FOR LEAK,S. {MxOrder - 2001-1920000586 / 1Emergency CM Operations Tx GSU} | DIETZ, TERRY | Operations | Lite Truck |  | Lite Truck | Manual |  |  | 2001-10-19 10:24 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1920000319 | 1Emergency CM Operations Tx GSU | Unclassified | 4-4-00 DBTGD WINDING TEMP. GAUGE NEEDS RECALIBRATED PLANT PERSONAL SAID FANS COMING ON LATE ALARMING EARLY-- GLEN, YOU MIGHT WANT TO SEND THIS TO CHIP, K.A.S. 4/12/OO GAUGE WAS REPAIRED BY JIM URBANIK. {MxOrder - 2000-1920000319 / 1Emergency CM Operations Tx GSU} | KELLY, GLENN | Operations | Shows - Preview |  | Lite Truck | Manual |  |  | 2000-04-07 08:16 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2005-1910000468 | 1Emergency CM Operations Tx GSU | Unclassified |  |  | Operations | Lite Truck | P1 | Lite Truck | Manual | HENRY, ROSCO |  | 2005-10-10 08:13 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2001-1880000208 | 1Emergency CM Operations Tx GSU | Unclassified | 03/05/01 REPAIR B PHASE CONNECTOR BOLT LOCKED UP REMOVED RETAPED AND REPLACED WITH NEW BOLT..DBMWV. {MxOrder - 2001-1880000208 / 1Emergency CM Operations Tx GSU} | VAN GALDER, MARK | Operations | Maintenance 3 Man Crew |  | Maintenance 3 Man Crew | Manual |  |  | 2001-03-06 09:42 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2020-3000012318 | 1Emergency CM Operations Tx GSU | Unclassified | 11-10-20 Big Bend #1 & #2 nitrogen system low gas alarm. Crumpton Gas delivered bottle to wrong loction. Had to get electric shop to assist me in moving bottles to right location to C/O empty bottles. Absher [MxOrder - 2020-3000012318 / 1Emergency CM Operations Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P1 | Lite Truck | Manual | ABSHER, LARRY | 2020-11-10 09:22 | 2020-11-10 13:19 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 182 | [7 empty] | No Archive
2020-3000051236 | 1Emergency CM Operations Tx GSU | Unclassified | 5/30/20..Called for loss of AC.Both sources had good volltaged there was a light with a toggle switch I toggled the switch and light went out.Ran fans and pumps alarm clear...Crosby [MxOrder - 2020-3000051236 / 1Emergency CM Operations Tx GSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective |  | Lite Truck | Manual | CROSBY, KELLY |  | 2020-05-30 01:57 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 588 | [7 empty] | No Archive
2004-1940001028 | 1Emergency CM Operations Tx GSU | Unclassified | 3/2604. PLANT REPORTED LOW OIL FLOW ALARM. CLEARED. ALL PUMPS AND FANS ARE RUNNING. DBDKM. 3/30/04--The plant reported an oil flow alarm again. The fans and pumps were all running when I arrived, the alarm was in, in the cabinet. I re-set it and the alarm stayed clear. If this continues then I believe we have a sticking flow gauge. that comes in when the stand by bank of fans kicks in. We can check this in the morning before all the fans are running.---dbdkb [MxOrder - 2004-1940001028 / 1Emergency CM Operations Tx GSU] | BRYAN, DAVID | Operations | Lite Truck |  | Lite Truck | Manual | MCCATTY, DONALD |  | 2004-04-16 10:55 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2009-1930002635 | 1Emergency CM Operations Tx GSU | Unclassified | 08/21/09. Oil Temp. Alarm. All the fans running when I arrived. Alarm had cleared. Notified Palm River. dboxs Returned and met up with Mr. Urbanik to check out Unit alarms. dboxs 8/23/09 CHKed ALL ALMS WHILE DOING WE CHK. NONE WERE IN. DBMHC [MxOrder - 2009-1930002635 / 1Emergency CM Operations Tx GSU] | URBANIK, JAMES | Operations | Lite Truck | P1 | Lite Truck | Manual | SIERRA, OSCAR |  | 2009-08-23 22:41 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2006-1930001744 | 1Emergency CM Operations Tx GSU | Unclassified | 4/16/06 LOW OIL FLOW ALM. IN ON PANEL #2 CONTROL RM. #2FAN BANK AND PUMP NOT WORKING. GOT PRINTS AND FOUND NO VOLTAGE ON OUTLET SIDE OF CONTACTOR.TRIED TO RESET TWICE NO LUCK. THIRD TIME IT RESET. DBMHC [MxOrder - 2006-1930001744 / 1Emergency CM Operations Tx GSU] 4/16/ 06 ALM CAME IN AGAIN AT 1800 . THIS TIME ITS # 2 ; 4 ; AND 5 . RESET THEM AND CHECKED THEIR AMPS. THE BANKS WHICH ARE TRIPPING ARE PULLING MORE AMPS.BUT NOT ENOUGH TO CONSIDER THEM PROBMATIC. DBMHC 4/17/06 GOT CALLED OUT 5 HOURS LATER SAME PROBLEM THIS TIME , IM GOING TO STAY BECAUSE THE HIGH OIL TEMP, ALM IS ALSO IN . DBMHC AT 630 I AM TOLD BY D. MCCATTY I WILL BE RELEAVED BY GUS 4/17/06 PR. DISP. CALLED ME OUT FOR TEMP. ALM. RESET FANS 2 . 4 AND 5. DBMHC. 4/28/06. THE PLANT IS CHECKING ON PROBLEM WITH LOW VOLTAGE ON THE 480 FEED THAT POWERS THE #2-4-6 PUMPS AND FANS. THEY BELIEVE THERE IS A GROUND IN THE PLANT. 5-26-06 Oil temp alarm in, the oil temp guage read 75 c now and the drag hand was at 85 c.The winding temp was 85 c now and the drag hand was104 c.Volages are p1-p2 457, p2-p3 456, p1-p3 456, e1-e2 448, e2-e3 449 , e1-e3 448 .Reset oil temp alarm, gave readings to K. Harrell. gef 5/29/06JIM, CHECK TX TEMP---WINDING 100/105, OIL 85/85, 386MW, 40 VARS. ALL FANS AND OIL PUMPS RUNNING. | HARRELL, KENNETH | Operations | Lite Truck | P1 | Lite Truck | Manual | CHICO, MICHAEL |  | 2006-07-06 07:18 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
1999-1950000190 | 1Emergency CM Operations Tx GSU | Unclassified | CALLED TO PLANT FOR HI-WINDING TEMP. ALARM, TX. FINE, BAD ALARM CARD IN #1 CONTROL ROOM. DBGAM. 8/13/99. {MxOrder - 1999-1950000190 / 1Emergency CM Operations Tx GSU} | MILIAN, GYNARO | Operations | Lite Truck |  | Lite Truck | Manual |  |  | 1999-08-13 20:54 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1950000313 | 1Emergency CM Operations Tx GSU | Unclassified | PLANT COMPLAIN OF [1] FAN BANK DROPPING OUT AFTER A HOT SPOT ALARM CAME IN, THEY PLACED THE FANS IN MANUAL, AFTER I LOOKED THE FANS OVER [GENO] I SAW THE TEMP. FOR THE WINDING AT 95 DEG. C AND PLACED THE FANS IN AUTO, THE FANS STAYED ON,EVERTHING FINE, COMPLETED ON 4/1/00.DBGAM {MxOrder - 2000-1950000313 / 1Emergency CM Operations Tx GSU} | MILIAN, GYNARO | Operations | Lite Truck |  | Lite Truck | Manual |  |  | 2000-04-01 16:55 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2008-1950001955 | 1Emergency CM Operations Tx GSU | Unclassified | 11/24/08---LOW GAS ALARM ON TX CHANGED OUT 1 N2 BOTTLE.---DBRBC [MxOrder - 2008-1950001955 / 1Emergency CM Operations Tx GSU] |  | Operations | Lite Truck | P1 | Lite Truck | Manual | CHANCEY, RANDOLPH |  | 2008-11-26 08:39 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
1999-1960000159 | 1Emergency CM Operations Tx GSU | Unclassified | BIG BEND #2 GSU CHANGE OUT NITROGEN BOTTLE. M.LUPER 4/23/99 {MxOrder - 1999-1960000159 / 1Emergency CM Operations Tx GSU} | LUPER, MICHAEL | Operations | Lite Truck |  | Lite Truck | Manual |  |  | 1999-04-23 11:38 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1960000365 | 1Emergency CM Operations Tx GSU | Unclassified | 04/30/00 #2 MAIN TX. HIGH OIL TEMP. ALARM THE UNIT WAS NOT AT FULL LOAD. PALM RIVER HAD ME STAND-BY UNTIL THEY TOOK SOME MORE LOAD OFF.CLEAR ALARM TX. O.K. DBMGL. {MxOrder - 2000-1960000365 / 1Emergency CM Operations Tx GSU} | LUPER, MICHAEL | Operations | Lite Truck |  | Lite Truck | Manual |  |  | 2000-04-30 23:37 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1960000442 | 1Emergency CM Operations Tx GSU | Unclassified | 08/17/00 CHANGE OUT NITROGEN BOTTLE. DBMGL {MxOrder - 2000-1960000442 / 1Emergency CM Operations Tx GSU} | LUPER, MICHAEL | Operations | Lite Truck |  | Lite Truck | Manual |  |  | 2000-08-17 13:40 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2005-1980001305 | 1Emergency CM Operations Tx GSU | Unclassified | 6/9/05 oil flow alarm bank 2. the left thermal O.L. was triped for coolers 2,4,6 reset O.L. all fans & pumps ran OK . alarm cleared. Ph. to Ph. V. 456 , 456, 456 dbfgk 6/12/05---Oil flow alarm. I found the thermals tripped on the contactors for coolers 2,4 & 6. I reset them and checked the voltages across the phases and they were normal. I checked every leg on all 6 contactors and they were all using between 15 and 18 amps. The alarm reset and I notified Mr Medich and he is going to address this Monday morning. It has been raining a lot and there was no sign of water in the control cabinet.----dbdkb [MxOrder - 2005-1980001305 / 1Emergency CM Operations Tx GSU] | MCCATTY, DONALD | Operations | Lite Truck | P1 | Lite Truck | Manual | KINSMAN, FORREST (WOODY) |  | 2005-08-16 08:40 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2005-1980001374 | 1Emergency CM Operations Tx GSU | Unclassified | 9/28/05 had bank 2 oil flow alarm & bank 2 fans & PP. were not runing . reset the left thermal overloads on contactors 2,4,6.problem last happened on 6/12/05 . dbfgk [MxOrder - 2005-1980001374 / 1Emergency CM Operations Tx GSU] | KINSMAN, FORREST (WOODY) | Operations | Lite Truck | P1 | Lite Truck | Manual | KINSMAN, FORREST (WOODY) |  | 2005-09-28 14:58 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2005-1970001235 | 1Emergency CM Operations Tx GSU | Unclassified | 1/4/05 Suspect bad fan on top of west bank , need two people to work on.DBJOD....... 1/5/05 REMOVED FAN FROM MOTOR . DISCONECTED MOTOR. ORDERED MOTOR. DBFGK 1/6/05 installed motor & fan . took old motor to shop. to be repaired & put in stock. dbfgk [MxOrder - 2005-1970001235 / 1Emergency CM Operations Tx GSU] | KINSMAN, FORREST (WOODY) | Operations | Berry - Preview | P1 | Lite Truck | Manual | DUKES, JAMES |  | 2005-01-06 12:06 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2005-2980000754 | 1Emergency CM Operations Tx GSU | Unclassified |  | SMITH, GREGORY | Operations | Lite Truck |  | Lite Truck | Manual | SMITH, GREGORY |  | 2005-02-07 22:21 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2009-2890001742 | 1Emergency CM Operations Tx GSU | Unclassified | 4/21/09 I WAS SENT TO BIG BEND #2 GSU .BECAUSE PLANT WAS CONCERNED ABOUT THE NOISE BANKs 1 + 4 WERE MAKING. BY DISCONNECTING THE FANS ONE AT A TIME I ISOLATED THE NOISEY FANS TO THE MID FAN IN BANK 4 AND THE TOP FAN IN BANK 1. THESE FANS ARE NOISEY BECAUSE I BELIEVE THEIR BEARINGS ARE GOING OUT, ALL READY. BOTH THESE FANS ARE IN GROUP 2 SO I PUT THE TX IN #I UNTIL I CAN TALK TO D. MCCATTY AND SEE WHAT OUR OPTIONS ARE. DBMHC 4/24/09 Installed zerk fittings on the motor in Group 4. and pumped it full of grease. This quieted the the motor considerable. DBMHC 4/28/09 INSTALLED FITTINGS ON THE TOP FAN ON BANK #1. AND PUMPED IT FULL OF GREASE FAN IS MUCH QUIETER. ALSO STAGED THE LADDER THAT I USED AND WE BOUGHT FOR THE TX FANS UNDER THE GOLF CART SHELTER WEST OF #3 GSU. AND LOCKED IT DBMHC 9-18-09 Same complaint as above. DBRWA 9/25/09 0n #1 BK the top fan blade has come apart so I ve disconnected it til I can fix it. I ve also disconnected the mid fan on BK #4 . DBMHC 9/30/09 Removed the guard and fan blade from BK # 4 mid fan. I also remove the motor and installed the new one. , however,I need some seal tite fittings to make up the elec. conection. I will pick up here tomorrow. DBMHC. 10/20/09 Installed new fan motor on #4 bank middle position. ZWR 11/16/09 INSTALLED FAN BLADE AND HOOKED UP MOTOR. DBMHC. 01/26/10----I see there is a new motor on the ground for the top fan hole in #1 cooler. Mr Butera has gotten a new blade fabricated though it is only a 4 blade fan and the rest of the fans on the tx are 6 blade, Mr Urbanik said the fans are simular in performance and to use the 4 blade fan. This job will require two men to complete.-----dbdkb 2/5/10----Had an apprentice meet me with a knuckle boom truck to hoist the new motor up into the fan shroud. We got the motor mounted in place but could not hook up the cord because the old seal tight fitting was damage when the old motor was removed. We do not have this type of fitting on our trucks and I was able to get one from the Big Bend warehouse. The rain started to move in and we were forced to quit for the day.-----dbdkb 2/8/10---I completed installing the motor and blade and fan gaurd. The fan rotation was correct.-----dbdkb [MxOrder - 2009-2890001742 / 1Emergency CM Operations Tx GSU] | URBANIK, JAMES | Operations | Lite Truck | P3 | Lite Truck | Manual | CHICO, MICHAEL |  | 2010-02-08 17:29 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2009-2890001796 | 1Emergency CM Operations Tx GSU | Unclassified | 6/18/09 PR HAS A HI TEMP ALM ON #2 GSU. @ BB. ALM IS NOT IN ON THE TX ALM PANEL AND IS NOT IN #2 CONTROL RM IN THE PLANT. ONLY PR IS SHOWING THIS ALM. SPOKE WITH J. OSTEEN. WE AGREED RTU NEEDED TO LOOK INTO IT AT THAT END. DBMHC 10/27/09 REOPENED AS PER. J. URBANIK. P.R. HAD HIGH OIL TEMP. ALARM NO ALARM @ TX. OR #2 CONTROL RM. PH. # 48222. ONLY IN @ P.R. OIL TEMP. 70 DEG. C. WINDING TEMP. 95 DEG. C.. ADDVISED J. URBANIK & P.R. ALL FANS & PUMPS RUNNING. CHECKED STA. SER. TX. & RES. STA. SER. TX. FOR ALARMS NONE FOUND. TALKED WITH P.R. GSU LOADED UP. DBGHP 10/29/09 CHKed THE TX NO ALMs NOTED. 3 WEEKS AGO J. URBANIK GAVE ME A RELAY FOR PLANT ENG. TO I NSTALL THIS RESOLVED THE PROBLEM. DBMHC [MxOrder - 2009-2890001796 / 1Emergency CM Operations Tx GSU] | URBANIK, JAMES | Operations | Lite Truck | P1 | Lite Truck | Manual | CHICO, MICHAEL |  | 2009-10-29 14:33 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2004-2980000705 | 1Emergency CM Operations Tx GSU | Unclassified | 09-10-04 CALLED ON OIL TEMP. AL TX. WIND.TEMP. WAS 100 C. OIL TEMP. WAS 90 C. COOLERS ARE VERY DIRTY & NEED TO BE PER.WASHED CALLED BENSON HE SAID MEMO IT. DBAXR [MxOrder - 2004-2980000705 / 1Emergency CM Operations Tx GSU] | SHOWS, KENNY | Operations | Berry - Preview | P1 | Lite Truck | Manual | ROCAMORA, ALBERT |  | 2004-12-20 14:04 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2004-2980000706 | 1Emergency CM Operations Tx GSU | Unclassified | 09-15-04 GAS ALARM REPLACED NEG. BOTTLE & RESET AL. CK. WITH PR. AL. CLEARED DBAXR [MxOrder - 2004-2980000706 / 1Emergency CM Operations Tx GSU] |  | Operations | Lite Truck |  | Lite Truck | Manual | ROCAMORA, ALBERT |  | 2004-09-15 21:57 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2002-2890000671 | 1Emergency CM Operations Tx GSU | Unclassified | ALARM IN LAST NIGHT,PLANT TURNED BREAKER OFF ON BANK 3 AFTER TRYING TO RESET IT.FOUND BAD 480 VOLT 30 AMP BREAKER BAD MIDDLE FAN, RECEPTICLE, AND PLUG [MxOrder - 2002-2890000671 / 1Emergency CM Operations Tx GSU] |  | Operations | Maintenance 2 Man Crew |  | Maintenance 2 Man Crew | Manual | FERNANDEZ, GUSTAVO |  | 2002-06-21 15:45 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2006-2980000977 | 1Emergency CM Operations Tx GSU | Unclassified | oil flow alarm bank #2.on cooler #2-#4-#6 reset left thermal o.l. on contactors.clear alarm.contactors need to be look at. dbggs 03/18/06 alarm on tx. checked all voltages and amped fans and pumps, thermals tripped on banks from the plant. This came and went , the plant found a fuse that was getting hot and changed it out.gef ,vxw . 4/28/06. COOLER BANKS #2/4/6 TRIPPED WHILE WE WERE WASHING #2 GSU COOLERS. WE HAD LOW VOLTAGE ON TWO PHASES OF THE 480 FEED FROM THE PLANT. PLANT ELECTRICANS BELIEVE THEY HAVE A GROUND IN THE PLANT. THEY HAVE TALKED TO BILL FOWLER. D. MCCATTY. 5/16/06 Checked voltages with D.MCCATTY found one low phase and one high phase checking phase to ground. During that time something changed and voltages equalised at 260 vac. DBDMH. 5/22/06 Changed out #5 cooler breaker .DBDMH. 5 /26/06 Checked winding &oil temp. DBDMH. 5/28/06 Checked winding & oil temp.DBDMH. 6/7/06 Checked temperature,oil 74 &winding 91 at 1500. DBDMH. 6/19/06 Checked temperature found winding at 92 and oil at 72 at 1900 hrs.DBDMH. 6/22/06 Checked temperature and found actual and drag the same, oil was 81 & winding 104 at 1730 hrs.DBDMH.7/27/06 Checked oil temp. alarm pumps and fans running.DBDMH.7/31/06 Checked oil temp. DBDMH. 8/8/06 Checked temp. found oil at 84 and winding at 100 at 1800 PM. DBDMH. 8-18-06 WINDING TEMP. 95-103 ,OIL 78-85.ON 8-17. [MxOrder - 2006-2980000977 / 1Emergency CM Operations Tx GSU] 5/12/06 P.R. DISP. SENT ME TO BB # 2 TX FOR ALM. THESE SAME FAN BANKS WERE OUT. I RESET AND MONITORED FOR A HALF. HOUR. DMHHC. 5-17-06 CHANGED OUT THERMALS ON THE LEFT SIDE OF 2,4 AND 6 CONTACTORS. CHANGED OUT BOTH ON 5. CHECKED VOLTAGES EVERYTHING CHECKED GOOD.GEF /DM. 5/18/06JIM, THERMALS TRIPPED ON 2,4,6, FAN BANK. LOW VOLTAGE ON E BLOCK. FOUND SAME IN POWER PLANT 480 VOLT BREAKER IN PLANT. CONTACT PLANT ELECTRICIAN AND SPO AND SHOWED PROBLEM IN PLANT . LOW VOLTAGE ON PHASE CAUSING THERMAL TO TRIP. PLANT ELECTRICIAN WORKING ON . BANK 2 480 CB IS OFF ALL FAN RUNNING AND MAINTAINING OF 480 FEED FROM BANK1 AND SWAPPOVER IN TX CABINET. NOTIFIED D. MCCATTY AND CHIP HALL. PLANT REPAIRED BANK 2 480 FEED IN PLANT. ALL FANS AND PUMPS RUNNING 5/20/06JIM, CALL OUT HIGH OIL TEMP. ALL FANS AND PUMPS RUNNING. NOTIFIED CONTROL ROOM AND SPO OIL TEMP HAS TO DROP 5 TO 8 DEG. BELOW ALARM POINT TO CLEAR ALARM. TEMP IS COMING DOWN PER CONTROL ROOM OPERATOR. 6/20/06JIM, CHECK TEMP. FOR MCCATTY. OIL AT 75 WINDING AT 95, 425 MW ON GENERATOR 150 VARS ON MACHINE 6/23/06JIM, CHECK TEMP. FOR MCCATTY. OIL AT 75, DRAG HAND AT 82. WINDING AT95, DRAG HAND AT 105.. 7/13/06 WINDING TEMP 90 -105, OIL 70 -82 ,RESET DRAG HANDS.GF 7/21/03 WINDING90-100,OIL 70-80.GEF 8-24-06 WINDING 85-100, OIL 70-83. 9-8-06 " 85-95 , " 68-73. 9-14-06 " 83-90 , " 67-72. 10-6 85-90 , 65-72 10-13 70-90, 63-73 10-20 70-75, 60-65 11-2 80-92,60-70 5/29/07---winding 98/106 liquid 83/97 Oil temp. alarrm was in with the oil temp. in at 83 degrees according to Mr Nelson it should be set at 90 degrees for the alarm point. It is set at 84 degrees now. Notified Mr McCatty and Mr Hall. Alarm would not clear.-I changed the alarm set point from 84 to 90 degrees as per Mr Hall and David Nelsons records. The alarm cleared. No alarms were in when I left but the oil temp. was already nearing the alarm point.--dbdkb Checked temps at about 1030. WT-92 LT-73 Drag hands were WT-100 LT-80 6-23-07 DBCWB . WT-102/86 LT-80/70 8-3-07 1130 hrs. DBCWB . At 1435 hrs. the WT was 102/88 and the LT was 80/70 DBCWB 8-15-07 | MCCATTY, DONALD | Operations | Lite Truck | P3 | Lite Truck | Manual | SMITH, GREGORY |  | 2009-02-10 17:02 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | 698264 | [6 empty] | No Archive
2010-2980001533 | 1Emergency CM Operations Tx GSU | Unclassified | 8/19/10 #2 GSU IS IN ALM FOR LO OIL FLOW. FLO - GAUGE IS STICKING. ABLE TO CLEAR ALM AFTER TAPPING ON THE SIDE OF THE GAUGE. PLEASE REPLACE THE #1 FAN BK GAUGE IN THE AM. AS PER D. MC CATTY. DBMHC 8/25/10------Replace flow gauge (Teco part #651 0854)on cooler # 1. Then cleared the alarm and checked with the control room and the alarm was clear there also.-----dbdkb asmdm [MxOrder - 2010-2980001533 / 1Emergency CM Operations Tx GSU] | URBANIK, JAMES | Operations | Lite Truck | P1 | Lite Truck | Manual | CHICO, MICHAEL |  | 2010-08-25 08:40 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-2990015573 | 2Planned CM Operations Tx GSU | Unclassified | 5/23/2000-Repair door latch on cabinet located on the west side of unit. Work is in preparation for storm season. Reference plant work order 1442-961-1. Work need to be done by June 1.-whdtc 4/26/2001 DBTGD INSTALLED HASP ON NIT. CABINET. JOB COMPLETE............. {MxOrder - 2000-2990015573 / 2Planned CM Operations Tx GSU} | DIETZ, TERRY | Operations | Lite Truck |  | Lite Truck | Manual |  |  | 2001-04-26 11:15 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1980000293 | 2Planned CM Operations Tx GSU | Unclassified | 5-17-00 HIGH OIL TEMP. ALARM @ 1905 OIL 85 WINDING 100 400 MW 70MVAR REDUSED TO 0 MVAR 410 M W ALL FANS & PUMPS RUNING ALARM CLEARED COMPLETE DBFGK {MxOrder - 2000-1980000293 / 2Planned CM Operations Tx GSU} | SHOWS, KENNY | Operations | Lite Truck |  | Lite Truck | Manual |  |  | 2000-05-17 02:01 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2004-1980001109 | 2Planned CM Operations Tx GSU | Unclassified | 6-27-04 DELIVER 3 FULL NITROGEN CYL. & PICK-UP 3 EMPY AT BIG BEND PLANT NEXT TO 2 GSU AT CARDOX CO2 TANK DBFGK [MxOrder - 2004-1980001109 / 2Planned CM Operations Tx GSU] | MCLEOD, RALPH | Operations | Berry - Preview | P3 | Lite Truck | Manual | KINSMAN, FORREST (WOODY) | 2004-07-13 08:36 | 2004-08-19 16:08 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2000-1960000451 | 2Planned CM Operations Tx GSU | Unclassified | 090/08/00 CHANGE OUT NITROGEN BOTTLE. DBMGL {MxOrder - 2000-1960000451 / 2Planned CM Operations Tx GSU} | LUPER, MICHAEL | Operations | Lite Truck |  | Lite Truck | Manual |  |  | 2000-09-08 09:11 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2004-1950001183 | 2Planned CM Operations Tx GSU | Unclassified | 11/6/04 PR CALLED SAID #2 MAIN TX HAD A BANK OF FANS NOT WORKING. FOUND CB TRIPPED IN CONTROL CAB RESET CB. ALL FANS AND PUMPS RUNNING BUT BOTTOM FAN ON BANK #2. MEGGERED FAN MOTOR IT IS BAD. FAN NEEDES TO BE REPAIRED AND REPALCED. CHECKED VOLTAGE AT OUTLET HAD 480VAC. HUNG TAG ON FAN. DID NOT PULL FAN AS PER ON CALL FOREMAN. DBGH 11/8/04--WE ORDERED A REPLACEMENT MOTOR BEFORE WE LEFT THE SHOP. REMOVED THE OLD MOTOR, IT TESTED OK BUT THE BEARINGS WERE VERY TIGHT.WE FOUND THE CORD BURNED OPEN AND REPLACED THE CORD AND PLUG AND INSTALLED THE NEW MOTOR. WE CHECKED THE ROTATION ALL WAS OK. WE RETURNED THE OLD MOTOR TO THEN SHOP FOR REPAIR ( ITS TAGGED)---COMPLETED---DBDKB [MxOrder - 2004-1950001183 / 2Planned CM Operations Tx GSU] | BERRY, STEVE | Operations | Lite Truck | P1 | Lite Truck | Manual | PAUL, GILBERT |  | 2004-11-08 14:55 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2006-1920001500 | 2Planned CM Operations Tx GSU | Unclassified |  | HARRELL, KENNETH | Operations | Lite Truck | P2 | Lite Truck | Manual | URBANIK, JAMES |  | 2006-05-01 07:55 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2001-1920000476 | 2Planned CM Operations Tx GSU | Unclassified | . 2/23/2001 DBTGD AS REQUESTED BY MR.KELLY, 5 OUT OF 6 1 in BALL VALVE.S ARE LEAKING,NEED TO BE REPLACED ALSO TEMP.GAUGE WELLS ARE LEAKING. TX NEED,S TO BE PRESSURE WASHED & 55 GAL. DRUM ( JUNK OIL ) CAN BE REMOVED AFTER JOB IS COMPLETE.... .ROCKS AROUND TX ARE OIL SOAKED, NEED TO BE REPLACED.....change out all six ball valve.dbggs 03/02/01 Please have oil stained dirt and rocks replaced berryCalled Building Ser. 3-19-01WULEO {MxOrder - 2001-1920000476 / 2Planned CM Operations Tx GSU} | ODOM, LYN | Operations | Maintenance 4 Man Crew |  | Maintenance 4 Man Crew | Manual |  | 1/1/1800 00:00 | 2001-03-23 10:23 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2012-3000020170 | 2Planned CM Operations Tx GSU | Unclassified | 3-27-12 dbrsc k q bad contactor on # 2 fans / c/o contactor fans pump ran good [MxOrder - 2012-3000020170 / 2Planned CM Operations Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P1 | Lite Truck | Manual | COLEMAN, STEVE |  | 2012-03-27 13:21 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2013-3000020576 | 2Planned CM Operations Tx GSU | Unclassified | 4-24-13 dbrsc jc replaced coil on swap over from 575 600 to 480 600 volt coil while tx was out for outage [MxOrder - 2013-3000020576 / 2Planned CM Operations Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Lite Truck | Manual | COLEMAN, STEVE | 2013-04-24 12:58 | 2013-04-24 13:04 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2013-3000020730 | 2Planned CM Operations Tx GSU | Unclassified | 8-12-13 B1201494 dbrsc c/o voltage relay for fans and pumps [MxOrder - 2013-3000020730 / 2Planned CM Operations Tx GSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Lite Truck | Manual | COLEMAN, STEVE |  | 2013-08-12 15:42 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2007-2990054943 | 2Planned CM Operations Tx GSU | Unclassified | 9/22/07JIM, INSTAL GROUNDS ON TX FOR OPERATIONS [MxOrder - 2007-2990054943 / 2Planned CM Operations Tx GSU] |  | Operations | Maintenance 2 Man Crew | P2 | Maintenance 2 Man Crew | Manual | URBANIK, JAMES |  | 2007-09-29 19:06 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | 859135 | [6 empty] | No Archive
2006-2990047967 | DOBLE PM 230 McEd C-03319-5-1 | Unclassified |  | VAN GALDER, MARK | Diagnostic | Doble 4 Man Crew | P3 | Doble 4 Man Crew | Manual | KELLY, GLENN | 2006-02-03 16:24 | 2006-06-15 05:25 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2009-2990063090 | DOBLE PM 230 McEd C-03319-5-1 | Unclassified |  | RAULERSON, GARY | Diagnostic | Doble 4 Man Crew | P3 | Doble 4 Man Crew | Manual | KELLY, GLENN | 2009-03-30 11:17 | 2009-03-31 19:40 | BIG BEND UNIT 2 | Y | 1 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2001-2990020242 | DOBLE PM 230 McEd C-03319-5-1 | Unclassified | 3-5-2001--completed doble test--OK--dbmwv {MxOrder - 2001-2990020242 / DOBLE PM 230 McEd C-03319-5-1} | VAN GALDER, MARK | Diagnostic | Doble 4 Man Crew |  | Doble 4 Man Crew | Manual |  |  | 2001-03-05 16:09 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2003-2990033035 | DOBLE PM 230 McEd C-03319-5-1 | Unclassified |  | CHANCEY, RANDOLPH | Diagnostic | Doble 4 Man Crew |  | Doble 4 Man Crew | Automatic | KELLY, GLENN |  | 2003-08-13 16:28 | BIG BEND UNIT 2 | Y | 1 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2019-3000260943 | DOBLE PM 230 McEd C-03319-5-1 | Unclassified | 7/10/20 All test with in range...Garland |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive |  | Doble 4 Man Crew | Automatic | SMOG, SMOG |  | 2020-07-10 13:49 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 67691 |  |  |  | 2019-02-18 | -1470 | 2019-02-18 | 0 | No Archive
2011-3000181955 | DOBLE PM 230 McEd C-03319-5-1 | Unclassified |  |  | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Doble 4 Man Crew | Manual | JEFFERSON, LANA |  | 2012-04-27 13:51 | BIG BEND GIF | Y | 1 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2015-3000229575 | DOBLE PM 230 McEd C-03319-5-1 | Unclassified |  |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive | P3 | Doble 4 Man Crew | Manual | KELLY, GLENN | 2015-01-22 08:37 | 2015-01-23 14:44 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2018-3000256247 | DOBLE PM 230 McEd C-03319-5-1 | Unclassified |  |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive | P3 | Doble 4 Man Crew | Automatic | SMOG, SMOG |  | 2016-02-19 10:54 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 27528 |  |  |  | 2018-01-22 | -1862 | 2018-01-22 | 0 | No Archive
2000-2990017134 | DOBLE PM 230 McEd C-03319-5-1 | Unclassified | 10/12/00 complete doble test==dbrbc {MxOrder - 2000-2990017134 / DOBLE PM 230 McEd C-03319-5-1} | CHANCEY, RANDOLPH | Diagnostic | Doble 4 Man Crew |  | Doble 4 Man Crew | Forecast Activation |  | 1/1/1800 00:00 | 2000-10-17 06:07 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
1999-2990012251 | DOBLE PM 230 McEd C-03319-5-1 | Unclassified | 10-28-99 DOBLE GOOD AND COMPLETE {MxOrder - 1999-2990012251 / DOBLE PM 230 McEd C-03319-5-1} | SMITH, LARRY | Diagnostic | Doble 4 Man Crew |  | Doble 4 Man Crew | Manual |  | 1/1/1800 00:00 | 1999-10-28 17:03 | BIG BEND | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
1999-2990012741 | COOLER WASHING PM 230 McEd C-03319-5-1 | Unclassified | COMPLETED COOLER WASHING #2 GSU . 02/15/00 DBKDH {MxOrder - 1999-2990012741 / COOLER WASHING PM 230 McEd C-03319-5-1} | HARRELL, KENNETH | Maintenance | Lite Truck |  | Lite Truck | Forecast Activation |  | 2000-02-03 | 2000-02-16 13:57 | BIG BEND | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2018-3000260002 | COOLER WASHING PM 230 McEd C-03319-5-1 | Unclassified |  |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive |  | Maintenance 1 Man Crew | Automatic | SMOG, SMOG |  | 2019-03-05 08:05 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 39816 |  |  |  | 2018-12-16 | -1534 | 2018-12-16 | 0 | No Archive
2014-3000226703 | COOLER WASHING PM 230 McEd C-03319-5-1 | Unclassified | 12/15/16 Coolers have been cleaned. Dukes |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive | P3 | Maintenance 1 Man Crew | Automatic | JEFFERSON, LANA |  | 2016-12-16 10:45 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 11268 |  |  |  | 2014-08-02 | -3131 | 2014-08-02 | 0 | No Archive
2004-2990039517 | COOLER WASHING PM 230 McEd C-03319-5-1 | Unclassified | 10-25-04 REMOVED SHROUDS AND WRAPED MOTORS FOR PREP FOR COOLER WASHING. dbger 10-26-04 ASSISTED GLADIATOR AND PUT BACK TO NORMAL. dbger. [MxOrder - 2004-2990039517 / COOLER WASHING PM 230 McEd C-03319-5-1] |  | Maintenance | Maintenance 1 Man Crew |  | Maintenance 1 Man Crew | Automatic | KELLY, GLENN |  | 2004-10-26 16:42 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2001-2990019010 | COOLER WASHING PM 230 McEd C-03319-5-1 | Unclassified | 3/12/01JIM COMPLETE COOLER WASHING {MxOrder - 2001-2990019010 / COOLER WASHING PM 230 McEd C-03319-5-1} | URBANIK, JAMES | Maintenance | Lite Truck |  | Lite Truck | Automatic |  |  | 2001-03-12 16:36 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2002-2990024660 | COOLER WASHING PM 230 McEd C-03319-5-1 | Unclassified |  | BRYAN, DAVID | Maintenance | Maintenance 1 Man Crew |  | Maintenance 1 Man Crew | Automatic | URBANIK, JAMES |  | 2002-04-08 11:33 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2008-2990058622 | COOLER WASHING PM 230 McEd C-03319-5-1 | Unclassified |  |  | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Maintenance 1 Man Crew | Automatic | JEFFERSON, LANA |  | 2012-08-02 12:29 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2006-2990049705 | COOLER WASHING PM 230 McEd C-03319-5-1 | Unclassified | Manually created to reset triggers since 6/1/06 Cooler Washing was completed per G.Paul. See "CM" 2006-2990049025 - mml [MxOrder - 2006-2990049705 / COOLER WASHING PM 230 McEd C-03319-5-1] | PAUL, GILBERT | Maintenance | Maintenance 1 Man Crew | P3 | Maintenance 1 Man Crew | Manual | LOFTON, MOLLY |  | 2006-06-01 15:53 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2013-3000020462 | 2Planned CM Oil Leaks - TxGSU | Unclassified | B 1201367 GSU #2 CLEANED UP OIL AND PADS AROUND TX. TIGHTENED UP FLANG ON BANK # 4 20-14 DBRSC ADDED 2 FUNNEL TO RAD FLANGED TRY TO TIGHTED FLANGE AND YELLOW DRUM C/O PADS IN OTHER PADS SPRAYED DOWN AND CLEANED SIDE TX 2/26/15 C/O oil pads.CIJLC 3/5/15 Called for emergency oil clean up, washed down and changed out pads. CIJLC [MxOrder - 2013-3000020462 / 2Planned CM Oil Leaks - TxGSU] |  | Gen Interconnect Facility | Lite Truck | P3 | Lite Truck | Manual | COLEMAN, STEVE |  | 2016-01-08 09:57 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 5887 | [7 empty] | No Archive
2011-3000080042 | 2Planned CM Oil Leaks - TxGSU | Unclassified | 8-5-1 ( leave w o open ) OIL PUMP #6 IS LEAKING. I CLEANED & PUT A PAN UNDER IT. ROCK 10-10-11 #4 PUMP LEAKING INSTALLED PAN UNDER PUMP. ROCK 1-5-12 dbrsc replaced pads 01/20/12 repleaced oil pads dbrsc, jr [MxOrder - 2011-3000080042 / 2Planned CM Oil Leaks - TxGSU] 12/20/12 CHANGED OUT OIL PADS,ADDED 55 GALLON DRUM, LEAK IS BAD. RSC/JLC |  | Gen Interconnect Facility | Maintenance 3 Man Crew | P3 | Maintenance 3 Man Crew | Manual | ROCAMORA, ALBERT | 2011-08-05 10:46 | 2016-01-08 09:58 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 5887 | [7 empty] | No Archive
2017-3000022646 | 2Planned CM Oil Leaks - TxGSU | Unclassified | 3-1-17 sc rad flanges are leaking tighted up flangeds and there are pans already down washed down tx and pad put down more pads and pad 3-6-17 sc c/o pads drained oil out of pans 3-30-17 sc c/o pads drain pans got 3 gal of oil 4-6-17 sc jg c/o pads dain oil pans 5-2-17 sc drained4 gals of oil out of pans washed down pad c/o pads 5-5-17 sc c/o pads cleaned up oil on pad and drained pans [MxOrder - 2017-3000022646 / 2Planned CM Oil Leaks - TxGSU]5-17-17 drain pans c/o pads 6-13-17 sc washed pump and flanges and c/o pads 6-28-17 sc rc c/o pads c/ u oil 7-3-17 sc c/opads drain pans 7-7-17 sc c/o pads drain out oil pans 7-20-17 sc c/o pads drained pans c/u oil 7-28-17 sc c/o pads c/u oil... .Drain oil out of pans and c/o pads 8-1-17..SC/KC...8-3-17 drain pans and c/o pads and cleaned up oil..SC/KC contractor regasket tx have bottom rad flange slow leak put down pads 1-11-18 sc rc c/o pads 3-6-20 closed work order & created a new one Absher |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P3 | Maintenance 3 Man Crew | Manual | COLEMAN, STEVE |  | 2020-03-06 07:54 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 64480 | [7 empty] | No Archive
2020-3000012173 | 2Planned CM Oil Leaks - TxGSU | Unclassified | 3-1-17 sc rad flanges are leaking tighted up flangeds and there are pans already down washed down tx and pad put down more pads and pad 3-6-17 sc c/o pads drained oil out of pans 3-30-17 sc c/o pads drain pans got 3 gal of oil 4-6-17 sc jg c/o pads dain oil pans 5-2-17 sc drained4 gals of oil out of pans washed down pad c/o pads 5-5-17 sc c/o pads cleaned up oil on pad and drained pans [MxOrder - 2017-3000022646 / 2Planned CM Oil Leaks - TxGSU]5-17-17 drain pans c/o pads 6-13-17 sc washed pump and flanges and c/o pads 6-28-17 sc rc c/o pads c/ u oil 7-3-17 sc c/opads drain pans 7-7-17 sc c/o pads drain out oil pans 7-20-17 sc c/o pads drained pans c/u oil 7-28-17 sc c/o pads c/u oil... .Drain oil out of pans and c/o pads 8-1-17..SC/KC...8-3-17 drain pans and c/o pads and cleaned up oil..SC/KC contractor regasket tx have bottom rad flange slow leak put down pads 1-11-18 sc rc c/o pads 3-6-20 In process of cleaning up oil leaks, & digging up rocks. also added oil drip pans. I have to come back & dig up oily rocks,called off. Absher 3-9-20 dug out some oily rocks Absher / Tomlinson 5-29-20 closed & created new work order Absher [MxOrder - 2020-3000012173 / 2Planned CM Oil Leaks - TxGSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P3 | Maintenance 3 Man Crew | Manual | ABSHER, LARRY | 2020-03-06 07:53 | 2020-05-29 08:30 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 67691 | [7 empty] | No Archive
2018-3000051029 | 2Planned CM Oil Leaks - TxGSU | Unclassified | 12/27/18..Called for oil leak coming from winding temp probe looks like flange is leaking need a outage to either tighten up flange or drop oil level to replace gasket.I cleaned up oil and cleand up rocks and put pads down...Crosby 12/28/18..There was a steady drip coming from flange clleaned and put loctite flange and it dryed might have slow down the leak or stop it.Will check Monday to see it its still leaking.Crosby 1/2/19..Still leaking cleaned and put magic bond let it set and cleaned oil and c/o pads.Checked before leaving looked like it stop...KC/MTM 1-24-19- cleaned oil and c/o pads. 4-3-19- cleaned oil and c/o pads. mtm 11-19-19- unit is off line and leaking oil. cleaned up oil, c/o pads, put drip pans down and tightened up flanges. will monitor...mtm 5-29-20 closed & created a new work order Absher [MxOrder - 2018-3000051029 / 2Planned CM Oil Leaks - TxGSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective |  | Maintenance 3 Man Crew | Manual | CROSBY, KELLY | 2018-12-27 18:39 | 2020-05-29 08:29 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 67691 | [7 empty] | No Archive
2000-2990014803 | 2Planned CM Oil Leaks - TxGSU | Unclassified | various oil valves leaking, bucket under north side valves, make necessary repairs. check all cooler valves.08-23-00--WWK--Cleaned valves -- oil soaked rocks below them need to be removed & replaced-- 2/23/2002 TGD UPDATED MEMO WITH MORE INFO 2001 1920000476 57000 601 CLOSING THIS MXORDER {MxOrder - 2000-2990014803 / 2Planned CM Oil Leaks} | SMITH, GREGORY | Maintenance | Shows - Preview |  | Maintenance 4 Man Crew | Manual |  | 1/1/1800 00:00 | 2001-02-23 12:41 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2006-2890001374 | 2Planned CM Oil Leaks - TxGSU | Unclassified | #2 PUMP IS LEAKING OIL AT THE PLUG THAT IS MOUNTED TO THE PUMP FROM THE PROBES.(A STEADY STREAM WHEN THE ELECTRICAL PLUG IS REMOVED).PUT A PAN , OIL SOAK PADS AND BUCKET UNDERNEATH. CLOSED RADIATOR BUTTERFLIES OFF AT THE TOP AND BOTTOM.THE LEAK IS A SLOW DRIP NOW.DRAINED 5 GALLONS OF OIL FROM THE BOTTOM OF THE RAD. DOES NOT SEEM LIKE THE BUTTERFLIES ARE HOLDING.NEED TO REPLACE PUMP . SPOKE WITH GEORGE AND DONNIE.GEF 7/21/06 Disconnected wire from pump and clamped hose over receptacle on motor and was able to stop leak. Need to monitor to make sure it stays dry. DBDMH. 7/22/06--I checked the oil leak as requested by Medich. Just a small amount of oil in the 5gal. bucket ( approx. a cup ). Cleaned out. No visble oil at the temp. repair on the pump.---dbdkb 7-25-06 CHECKED BUCKET ,DRY AND THE TEMP STOP LEAK IS HOLDING.GEF 8-18-06 BREAKER WAS CLOSED ON BANK 2,FANS RUNNING. SPOKE WITH KENNY AND GEORGE,UNPLUGGED ALL FANS ON THE BANK AND CLOSED THE C.B. BACK IN TO CLEAR THE GENERAL ALARM. CLEANED OUT PAN AND PUT NEW OIL PADS.GEF 9-18-06 dbrsc removed oil down passed top of rad pipe flanged . top rad valve would not hold. replaced plug on pump , cleaned pumps on tx.run all pumps and fans. [MxOrder - 2006-2890001374 / 2Planned CM Oil Leaks] | COLEMAN, STEVE | Maintenance | Maintenance 3 Man Crew | P1 | Maintenance 3 Man Crew | Manual | FERNANDEZ, GUSTAVO |  | 2006-09-19 14:05 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2009-2890001878 | 2Planned CM Oil Leaks - TxGSU | Unclassified | 11/29/09 #2 GSU, #4 COOLER IS LEAKING FROM THE DRESSER COUPLING. I TIGHTENED THE COUPLING TO STOP THE LEAK. THEN I CHKED THE OTHERS ON THIS GSU. I CLEANED UP THE OIL WHICH HAD ALREADY SPILT. I WILL LEAVE THIS MX OPEN AND RE CHK. IT MON TO MAKE SURE ITS NOT LEAKING. BEFORE I CLOSE IT OUT. DBMHC 12/1/09 cleaned up rocks and ck leak mx complete. DBMHC [MxOrder - 2009-2890001878 / 2Planned CM Oil Leaks] | URBANIK, JAMES | Maintenance | Lite Truck | P1 | Lite Truck | Manual | CHICO, MICHAEL |  | 2009-12-01 12:48 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2008-1970001802 | 2Planned CM Oil Leaks - TxGSU | Unclassified | 12/29/08 Transformer leaking from flanges. Put down oil pan and oil soak pads..DBJOD.. 1/5/09 Cleaned area put dn new diapers. DBMHC [MxOrder - 2008-1970001802 / 2Planned CM Oil Leaks] | HARRELL, KENNETH | Maintenance | Maintenance 3 Man Crew | P2 | Maintenance 3 Man Crew | Manual | DUKES, JAMES |  | 2009-04-21 18:05 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2020-3000012216 | 2Planned CM Oil Leaks - TxGSU | Unclassified | 5-29-20 #2 GSU has oil leaks all over, plant & substation has been notified for outage to regasket tx,oil clean up, added 15 more oil pans all around tx Absher 7/1/20 C/O PADS. GHP 7-9-20 C/O pads in pans Absher 8-6-20 C/O pads in pans Absher 9-18-20 C/O pads in pans Absher 9-24-20 C/O pads in pans Absher 10-9-20 C/O pads in pans Absher [MxOrder - 2020-3000012216 / 2Planned CM Oil Leaks - TxGSU] 1-21-21 closed, created new work order Absher |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P3 | Lite Truck | Manual | ABSHER, LARRY | 2020-05-29 08:31 | 2021-01-21 10:23 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 672 | [7 empty] | No Archive
2021-3000012549 | 2Planned CM Oil Leaks - TxGSU | Unclassified | 5-29-20 #2 GSU has oil leaks all over, plant & substation has been notified for outage to regasket tx,oil clean up, added 15 more oil pans all around tx Absher 7/1/20 C/O PADS. GHP 7-9-20 C/O pads in pans Absher 8-6-20 C/O pads in pans Absher 9-18-20 C/O pads in pans Absher 9-24-20 C/O pads in pans Absher 10-9-20 C/O pads in pans Absher [MxOrder - 2020-3000012216 / 2Planned CM Oil Leaks - TxGSU] 1-21-21 New work order 1-21-21 c/o oil pads & cleaned up oil Absher 2-18-21 c/o oil pads Absher 4-8-21 c/o oil pads Absher 4/29/21 C/O pads in pans Pearson/Absher [MxOrder - 2021-3000012380 / 2Planned CM Oil Leaks - TxGSU] 5-13-21 c/o oil pads Absher 5-27-21 c/o oil pads Absher 7-14-21 c/o oil pads Absher 07/23/21 c/o oil pads Absher, Richard 08/19/2021 C/O oil pads and clean up oil. Newsome 9-30-21 c/o oil pads & cleaned up oil Absher 10-14-21 c/o oil pads Absher 10-21-21 c/o oil pads Absher 10-26-21 c/o oil pads Absher [MxOrder - 2021-3000012549 / 2Planned CM Oil Leaks - TxGSU] 11-18-21 c/o oil pads Absher-Faison 12/10/21 Changed out oil pads Parker/Absher 12-16-21 C/O oil pads Absher 12-30-21 C/O oil pads Absher 1/6/22 C/O oil pads. CIJLC 1/13/22 C/O oil pads. CIJLC 1/20/22 C/O oil pads. CIJLC 1/27/22 C/O oil pads. CIJLC 2/3/22 C/O oil pads. CIJLC 2/28/22 Removed oil pans, TX No Oil. CIJLC |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P3 | Maintenance 3 Man Crew | Manual | ABSHER, LARRY | 2021-05-13 10:48 | 2022-06-20 13:07 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 1000 | [7 empty] | No Archive
2021-3000012380 | 2Planned CM Oil Leaks - TxGSU | Unclassified | 5-29-20 #2 GSU has oil leaks all over, plant & substation has been notified for outage to regasket tx,oil clean up, added 15 more oil pans all around tx Absher 7/1/20 C/O PADS. GHP 7-9-20 C/O pads in pans Absher 8-6-20 C/O pads in pans Absher 9-18-20 C/O pads in pans Absher 9-24-20 C/O pads in pans Absher 10-9-20 C/O pads in pans Absher [MxOrder - 2020-3000012216 / 2Planned CM Oil Leaks - TxGSU] 1-21-21 New work order 1-21-21 c/o oil pads & cleaned up oil Absher 2-18-21 c/o oil pads Absher 4-8-21 c/o oil pads Absher 4/29/21 C/O pads in pans Pearson/Absher [MxOrder - 2021-3000012380 / 2Planned CM Oil Leaks - TxGSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P3 | Lite Truck | Manual | ABSHER, LARRY | 2021-01-21 10:21 | 2021-05-13 10:48 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 233 | [7 empty] | No Archive
2008-1940002169 | 2Planned CM Oil Leaks - TxGSU | Unclassified | 08/03/08---While checking the GSU after I switched on unit #2, I noticed the rocks and steel structures on the south side of the GSU have an oil film on them as well as the south side of the tx. It has been raining this evening but the oil is obvious. There is standing water and or oil on the top of the tx between the center and west plant side bushings (ducts). Please have the tx looked at in the daylight to see where the oil is coming from. Also there is a 5 gallon bucket under one of the east coolers that has oil in it and it needs to be emptied.----dbdkb 8/4/08 REMOVED COVER FROM LB. ON SOUTH-WEST CORNER OF #2 GSU AS PER. D. MCCATTY. CLEANED INSIDE OF LB. WITH NO-FLASH FOLDED OIL SOAK PAD AND PUT INSIDE OF LB. TO CATCH ANY OIL PUT COVER BACK ON LB. DBGHP 9/26/08---While switching on unit #2 I noticed oil around the LB covers on the conduit on the side of the tx about 3 feet above the pad. I cleaned the side of the tx (front, west side, and rear) and picked up the old oil soak pads and put down new oil soak pads.----dbdkb 12/14/08 CALLED OUT TO #2 GSU FOR OIL LEAKING FROM TOP SUPPORT RIB S/E CORNER OF THE GSU. OIL IS STEADLY DRIPPING, 2 DROPS PER 10 SEC , AND HAS COATED THE TX , CONCRETE PAD AND ROCKS.CONTACTED S/S AS PER G. MEDITCH . OIL SPILL #SO-005-08 CLEANED UP AS BEST I COULD. RELEAVED N2 PSI FROM 1 TO 0, THIS SLOWED THE DRIP TO 1 A MIN.. I ISTALLED A BUCKET TO CATCH THIS. G. MEDITCH WILL HAVE SOMEONE CHECK IT TOMORROW. DBMHC 1-7-09 dbrsc cleanded up oil on ct box and tx cleanded out pan put in new pads [MxOrder - 2008-1940002169 / 2Planned CM Oil Leaks] | MCCATTY, DONALD | Maintenance | Maintenance 3 Man Crew | P1 | Maintenance 3 Man Crew | Manual | BRYAN, DAVID |  | 2009-04-21 18:05 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2010-1940002682 | 2Planned CM Oil Leaks - TxGSU | Unclassified | 4/21/10----Top flange on cooler #6 had a bad oil leak. We tightened the flange and cleaned the area. Put a pan and oil soak pads under the leak. Appears to have stoped the leak.----dbdkb mrm [MxOrder - 2010-1940002682 / 2Planned CM Oil Leaks] | BRYAN, DAVID | Maintenance | Maintenance 3 Man Crew | P1 | Maintenance 3 Man Crew | Manual | BRYAN, DAVID |  | 2010-04-21 15:45 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2005-1980001233 | OIL LEAKS CM - TxGSU | Unclassified | 1/10/05 small oil leak on # 1 cooler dresser coupling on the bottom of cooler. tightened bolts. cleaned off oil leak apeared to have stoped . will check tommorrow. dbfgk 1/12/05 NOT LEAKING. DBFGK [MxOrder - 2005-1980001233 / OIL LEAKS CM] | KINSMAN, FORREST (WOODY) | Maintenance | Lite Truck | P1 | Lite Truck | Manual | KINSMAN, FORREST (WOODY) |  | 2005-01-12 10:38 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
1999-2990009265 | OIL LEAKS CM - TxGSU | Unclassified | W.O. #19981395 - R. POTTER - 6/11/98 REPAIR OIL LEAK ON NEW DRAIN VALVE INSTALLED ON BANK # 5, FOR REMOVING OIL FROM COOLER.ALSO CHECK DRAIN VALVE BANK # 1 & 4. REPAIRED ALL VALVES EXCEPT 1 BOTTOM AND 2 TOP VALVES. WILL REQUIRE REMOVAL OF OIL FROM TX TO REPLACE REMAINDER OF VALVES. ALSO CHECK TOP OF TX FOR GAS LEAKS. valves on your desk bg- take small vac trailer-large pan-diapers 2/12/99 - TLT JOB COMPLETED 10-25-99 MCMINN {MxOrder - 1999-2990009265 / OIL LEAKS CM} | MCMINN, STEPHEN | Maintenance | Maintenance 3 Man Crew |  | Maintenance 3 Man Crew | Manual |  | 1/1/1800 00:00 | 1999-10-25 16:33 | BIG BEND | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2015-3000021818 | OIL LEAKS CM - TxGSU | Unclassified | 8-18-15 dbrsc putting on #2 unit gsu tx burnt up fan and motor contactors coils on bank 1 3 5 6 had to replace all [MxOrder - 2015-3000021818 / OIL LEAKS CM - TxGSU] |  | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective |  | Maintenance 3 Man Crew | Manual | COLEMAN, STEVE |  | 2015-08-18 14:09 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 4371 | [7 empty] | No Archive
2001-2990019839 | BUSHING CLEANING PM 230 GE M101676 | Unclassified | CLEAN GLASS ON TX.clean #3 standoff insulators & #1 bushing.03/ 01/01 completed cleaning the standoff insulators& geaseing them. clean all three highside bushing.dbggs--3-5-2001--GREASE HIGH SIDE BUSHINGS--DBMWV {MxOrder - 2001-2990019839 / BUSHING CLEANING PM 230 GE M101676} | SMITH, GREGORY | Maintenance | Maintenance 4 Man Crew |  | Maintenance 4 Man Crew | Manual |  | 1/1/1800 00:00 | 2001-03-05 16:12 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2002-2990030842 | BUSHING CLEANING PM 230 McEd C-03319-5-1 | Unclassified |  | MCMINN, STEPHEN | Maintenance | Doble 4 Man Crew |  | Doble 4 Man Crew | Automatic | KELLY, GLENN |  | 2002-12-21 15:55 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2006-2990047966 | BUSHING CLEANING PM 230 McEd C-03319-5-1 | Unclassified |  | VAN GALDER, MARK | Maintenance | Doble 4 Man Crew | P3 | Doble 4 Man Crew | Manual | KELLY, GLENN | 2006-02-03 16:24 | 2006-06-15 05:19 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2003-2990033036 | BUSHING CLEANING PM 230 McEd C-03319-5-1 | Unclassified |  |  | Maintenance | Doble 4 Man Crew |  | Doble 4 Man Crew | Related Independent | KELLY, GLENN |  | 2003-08-12 15:28 | BIG BEND UNIT 2 | N | 0 | 2003-2990033035 | Preventive Maintenance | 3862 | [7 empty] | No Archive
2009-2990063091 | BUSHING CLEANING PM 230 McEd C-03319-5-1 | Unclassified |  | RAULERSON, GARY | Maintenance | Doble 4 Man Crew | P3 | Doble 4 Man Crew | Related Independent | KELLY, GLENN | 2009-03-30 11:18 | 2009-03-31 19:53 | BIG BEND UNIT 2 | N | 0 | 2009-2990063090 | Preventive Maintenance | 3862 | [7 empty] | No Archive
2011-3000181956 | BUSHING CLEANING PM 230 McEd C-03319-5-1 | Unclassified |  |  | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Doble 4 Man Crew | Related Independent | JEFFERSON, LANA |  | 2020-07-07 13:56 | BIG BEND GIF | N | 0 | 2011-3000181955 | Preventive Maintenance | 67691 |  |  |  | 2014-03-30 | -3256 | 2014-03-30 | 0 | No Archive
2000-2990017136 | BUSHING CLEANING PM 230 McEd C-03319-5-1 | Unclassified | 10/12/00 clean & silicone #2 gsu==dbrbc {MxOrder - 2000-2990017136 / BUSHING CLEANING PM 230 McEd C-03319-5-1} | CHANCEY, RANDOLPH | Maintenance | Doble 4 Man Crew |  | Doble 4 Man Crew | Forecast Activation |  |  | 2000-10-12 18:04 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2000-2990017377 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified | 09/07/00 DGA/SCREEN TAKEN. DBMGL {MxOrder - 2000-2990017377 / DGA & Oil Screen PM Tx - TECO Lab} | LUPER, MICHAEL | Diagnostic | Lite Truck |  | Lite Truck | Automatic |  |  | 2000-09-07 12:56 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2021-3000271328 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified | 9-13-21 completed Absher |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive |  | Lite Truck | Automatic | SMOG, SMOG |  | 2021-09-13 11:12 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 323 |  |  |  | 2021-09-01 | -544 | 2021-09-01 | 0 | No Archive
2020-3000267464 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified | 9-17-20 completed Absher |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive |  | Lite Truck | Automatic | SMOG, SMOG |  | 2020-09-17 10:40 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 167 |  |  |  | 2020-09-01 | -909 | 2020-09-01 | 0 | No Archive
2019-3000263187 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified |  |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive |  | Lite Truck | Automatic | SMOG, SMOG |  | 2019-10-25 17:00 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 54433 |  |  |  | 2019-09-01 | -1275 | 2019-09-01 | 0 | No Archive
2014-3000227528 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified |  |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2014-09-22 13:15 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2015-3000232182 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified |  |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive | P3 | Lite Truck | Automatic | SMOG, SMOG |  | 2015-10-22 12:51 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 5016 |  |  |  | 2015-09-01 | -2736 | 2015-09-01 | 0 | No Archive
2013-3000220088 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified |  |  | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2013-10-22 18:14 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2012-3000185554 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified |  |  | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2012-09-26 10:27 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2017-3000254477 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified | 9-20-17 sc got oil sample |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive | P3 | Lite Truck | Automatic | SMOG, SMOG |  | 2017-09-20 11:54 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 18039 |  |  |  | 2017-09-01 | -2005 | 2017-09-01 | 0 | No Archive
2016-3000236365 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified | 9-19-16 sc got dga |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive | P3 | Lite Truck | Automatic | SMOG, SMOG |  | 2016-09-19 11:59 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 9614 |  |  |  | 2016-09-01 | -2370 | 2016-09-01 | 0 | No Archive
2018-3000258781 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified |  |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive |  | Lite Truck | Automatic | SMOG, SMOG |  | 2018-09-18 19:26 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 31409 |  |  |  | 2018-09-01 | -1640 | 2018-09-01 | 0 | No Archive
2009-2990061955 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified | 02/04/09 - To be used a 6 Month RETEST per K. Harrell also. Please use new sampling tube, new valve and clean syringe before sample is taken to cut down on retest per Medich - lkw 2/10/09 TOOK SAMPLE AS PER MX DBMHC [MxOrder - 2009-2990061955 / DGA & Oil Screen PM Tx - TECO Lab] | CHICO, MICHAEL | Diagnostic | Lite Truck | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2009-02-10 16:59 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2009-2990065441 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified |  |  | Diagnostic | Lite Truck | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2009-09-13 14:53 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2007-2990052628 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified | Please use new sampling tube, new valve and clean syringe before sample is taken to cut down on retest per Medich - lkw DGA and Oil Screen samples taken. 3-1-07 DBCWB . [MxOrder - 2007-2990052628 / DGA & Oil Screen PM Tx - TECO Lab] | BLEDSOE, CHARLES (WAYNE) | Diagnostic | Lite Truck | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2007-03-01 08:51 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2008-2990057135 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified | Please use new sampling tube, new valve and clean syringe before sample is taken to cut down on retest per Medich - lkw [MxOrder - 2008-2990057135 / DGA & Oil Screen PM Tx - TECO Lab] | KING, WILLIAM (BILLY) | Diagnostic | Lite Truck | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2008-02-03 10:20 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2006-2990047992 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified |  |  | Diagnostic | Lite Truck |  | Lite Truck | Automatic | KELLY, GLENN |  | 2006-02-23 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2003-2990036345 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified |  | URBANIK, JAMES | Diagnostic | Lite Truck |  | Lite Truck | Automatic | COLEMAN, STEVE |  | 2003-09-18 18:02 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2002-2990030357 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified |  | MCMINN, STEPHEN | Diagnostic | Lite Truck |  | Lite Truck | Automatic | KELLY, GLENN |  | 2002-09-12 09:15 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2004-2990041757 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified |  | KINSMAN, FORREST (WOODY) | Diagnostic | Lite Truck | P3 | Lite Truck | Automatic | KELLY, GLENN |  | 2005-02-02 12:02 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2001-2990023049 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified | 10-03-01--WWK--DGA Oil sample taken-- {MxOrder - 2001-2990023049 / DGA & Oil Screen PM Tx - TECO Lab} | KING, WILLIAM (BILLY) | Diagnostic | Lite Truck |  | Lite Truck | Automatic |  |  | 2001-10-03 10:07 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2010-2990070664 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified |  | BRYAN, DAVID | Diagnostic | Lite Truck | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2010-09-29 19:23 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2011-3000181018 | DGA & Oil Screen PM Tx - TECO Lab - TxGSU | Unclassified |  |  | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2011-09-15 14:53 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2016-3000233747 | DGA & Oil Screen CM Retest Tx - TECO Lab - TxGSU | Unclassified | Retest Oil Screen Only per K. Harrell - lkw 2-1-16 rsc got oil sample and oscar took it to lab [MxOrder - 2016-3000233747 / DGA & Oil Screen CM Retest Tx - TECO Lab - TxGSU] | COLEMAN, STEVE | Gen Interconnect Facility | B1201367 - GIF - Trans - Unplanned Maint - Corrective | P3 | Lite Truck | Manual | JEFFERSON, LANA |  | 2016-02-01 08:42 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 6178 | [7 empty] | No Archive
2016-3000234071 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified | 3-9-16 dbrsc got oil sample |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive | P3 | Lite Truck | Automatic | SMOG, SMOG |  | 2016-03-09 14:01 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 6649 |  |  |  | 2016-03-01 | -2554 | 2016-03-01 | 0 | No Archive
2013-3000187118 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified | OIL SAMPLE NOT TAKEN, CLOSED MX ORDER TO RESET TRIGGER, DGA AN OIL SCREEN ALSO TAKEN ON THIS DATE PER K. HARRELL - LKW [MxOrder - 2013-3000187118 / DGA PM Tx - TECO Lab - TxGSU] |  | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2013-10-22 18:15 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2012-3000183565 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified |  |  | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2012-03-18 10:05 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2014-3000223696 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified |  | COLEMAN, STEVE | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2014-05-05 11:45 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2015-3000229809 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified |  |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2015-03-17 15:27 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2019-3000261042 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified |  |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive |  | Lite Truck | Automatic | SMOG, SMOG |  | 2019-03-22 16:33 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 40759 |  |  |  | 2019-03-01 | -1459 | 2019-03-01 | 0 | No Archive
2018-3000256572 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified | 3/6/18 SC/Main complete |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive |  | Lite Truck | Automatic | SMOG, SMOG |  | 2018-03-06 11:45 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 23461 |  |  |  | 2018-03-01 | -1824 | 2018-03-01 | 0 | No Archive
2017-3000252692 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified |  |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive | P3 | Lite Truck | Automatic | SMOG, SMOG |  | 2017-03-02 13:10 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 12872 |  |  |  | 2017-03-01 | -2189 | 2017-03-01 | 0 | No Archive
2020-3000265381 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified | 3-9-20 completed Absher / Tomlinson |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive |  | Lite Truck | Automatic | SMOG, SMOG |  | 2020-03-09 11:17 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 64722 |  |  |  | 2020-03-01 | -1093 | 2020-03-01 | 0 | No Archive
2011-2990073331 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified |  |  | Diagnostic | Lite Truck | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2011-03-16 08:56 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2001-2990020215 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified | 4/10/2001 DBTGD DGA OIL SAMPLE TAKEN.... {MxOrder - 2001-2990020215 / DGA PM Tx - TECO Lab} | DIETZ, TERRY | Diagnostic | Lite Truck |  | Lite Truck | Automatic |  |  | 2001-04-10 11:35 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2003-2990032945 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified |  | URBANIK, JAMES | Diagnostic | Lite Truck |  | Lite Truck | Automatic | KELLY, GLENN |  | 2003-05-01 14:36 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2002-2990025318 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified |  | MCMINN, STEPHEN | Diagnostic | Lite Truck |  | Lite Truck | Automatic | KELLY, GLENN |  | 2002-04-01 10:45 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2005-2990044108 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified |  | KINSMAN, FORREST (WOODY) | Diagnostic | Lite Truck | P3 | Lite Truck | Automatic | KELLY, GLENN |  | 2005-04-25 12:54 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2004-2990038950 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified |  | BRYAN, DAVID | Diagnostic | Lite Truck |  | Lite Truck | Automatic | KELLY, GLENN |  | 2004-03-10 12:35 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2010-2990068126 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified |  | BRYAN, DAVID | Diagnostic | Lite Truck | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2010-03-10 15:39 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2009-2990065053 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified |  |  | Diagnostic | Lite Truck | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2009-08-29 18:10 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2008-2990059336 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified | Please use new sampling tube, new valve and clean syringe before sample is taken to cut down on retest per Medich - lkw [MxOrder - 2008-2990059336 / DGA PM Tx - TECO Lab] |  | Diagnostic | Lite Truck | P3 | Lite Truck | Automatic | JEFFERSON, LANA |  | 2008-08-03 13:50 | BIG BEND UNIT 2 | N | 0 |  | Preventive Maintenance | 3862 | [7 empty] | No Archive
2021-3000269453 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified | 3-4-21 completed Absher |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive |  | Lite Truck | Automatic | SMOG, SMOG |  | 2021-03-04 12:03 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 213 |  |  |  | 2021-03-01 | -728 | 2021-03-01 | 0 | No Archive
2022-3000273897 | TxGSU – Transformer Yearly Oil Test (DGA) | Unclassified | 4/22/22 GSU has NO OIL in it, was pumped dry a couple months ago. CIJLC |  | Gen Interconnect Facility | B1201494 - GIF - Trans - Insp Related Maint - Preventive |  | Lite Truck | Automatic | SMOG, SMOG |  | 2022-04-22 13:11 | BIG BEND GIF | N | 0 |  | Preventive Maintenance | 945 |  |  |  | 2022-03-01 | -363 | 2022-03-01 | 0 | No Archive
2006-2990049020 | DGA CM Retest Tx - TECO Lab - TxGSU | Unclassified | Get syringe and hand carry to CTL per J.Chacko request - mml 4/28/06 sample taken by Woodhouse and hand carried to lab [MxOrder - 2006-2990049020 / DGA CM Retest Tx - TECO Lab] | WOODHOUSE, DAVID | Diagnostic | Lite Truck | P1 | Lite Truck | Manual | LOFTON, MOLLY |  | 2006-05-01 07:58 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2006-2990049117 | DGA CM Retest Tx - TECO Lab - TxGSU | Unclassified | Created for history: Syringe sample requested by G.Medich and then hand carry to CTL for test results ASAP - mml Note: time charged to 2006-2890001349 mxorder for this syringe sample. [MxOrder - 2006-2990049117 / DGA CM Retest Tx - TECO Lab] | FERNANDEZ, GUSTAVO | Diagnostic | Lite Truck | P1 | Lite Truck | Manual | LOFTON, MOLLY |  | 2006-05-08 09:38 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive
2008-2990058344 | DGA CM Retest Tx - TECO Lab - TxGSU | Unclassified | 05/12/08-3 Month RETEST due to results from sample taken on 2/3/08 per K. Harrell. Please use new sampling tube, new valve and clean syringe before sample is taken to cut down on retest per Medich - lkw [MxOrder - 2008-2990058344 / DGA CM Retest Tx - TECO Lab] | KING, WILLIAM (BILLY) | Diagnostic | Lite Truck | P3 | Lite Truck | Manual | JEFFERSON, LANA |  | 2008-05-20 13:54 | BIG BEND UNIT 2 | N | 0 |  | Corrective Maintenance | 3862 | 914098 | [6 empty] | No Archive
2012-3000184863 | DGA CM Retest Tx - TECO Lab - TxGSU | Unclassified | 06/14/12- 3 Month RETEST per K. Harrell - lkw [MxOrder - 2012-3000184863 / DGA CM Retest Tx - TECO Lab - TxGSU] | COLEMAN, STEVE | Gen Interconnect Facility | Generation Interconnect Facilities | P3 | Lite Truck | Manual | JEFFERSON, LANA |  | 2012-07-16 12:50 | BIG BEND GIF | N | 0 |  | Corrective Maintenance | 3862 | [7 empty] | No Archive